## Slide 1: Substation Automation
Module 5: Substation Automation

## Slide 2: Presentation Overview
Part 1: Introduction to Substations
Part 2: Introduction to Substation Automation(SA)
Part 3: Evolution of SA
Part 4: SA and cyber security

## Slide 3: Part 1: Introduction to Substations

## Slide 4: What is a Substation?
Substations are assemblages of electrical components that form important links within the power system.
Electrical power passes through substations for the purpose of switching (connecting and disconnecting components, such as transmission lines), and to transform voltage (from high to low, or the reverse).
Power may go through several substations between generation and consumption, and change voltage in several steps.
http://www.blackhillsenergy.com/services/programs/electric-system.php

## Slide 5: Types of Substations
Distribution Substations
  Transfers power from transmission system to distribution system. Steps down voltage to value suitable for local usage.
Transmission Substations
  Steps up voltage from generation levels to transmission levels for transfer across long distances.
Switching Substations
  Operates at a single voltage level (no transformers) and switches operation of power lines.
Combination Substations
  Possesses any combination of functionalities defined for the previous three substation types.

## Slide 6: Distribution Substation
Main purpose is to step down the voltage from transmission levels to levels appropriate for local distribution.
May also isolate faults and/or regulate voltage.
Usually characterized by voltages up to 230 kV on the primary side and 12.5Y/7.2 kV, 13.2Y/7.6 kV, 13.8Y/8.0 kV, 24.9Y/14.4 kV, or 34.5Y/19.9 kV on the secondary side.
The power transformers commonly used in this application are two-winding type and may be single-phase or three-phase units.
http://www.blackhillsenergy.com/services/programs/electric-system.php

## Slide 7: Distribution Substation
Fig 1.1 : Basic Distribution Substation
The two primary distribution feeders of the substation illustrated in Figure 1.1 are protected by either power circuit breakers or automatic circuit reclosers.
Disconnect switches on both the source and load sides permit isolation during maintenance or other periods when complete de-energization is required.
The switches can be either single-pole, single-throw, hook stick-operated or three-pole, single-throw, group-operated, depending on the arrangement.

## Slide 8: Transmission Substation
Voltage is stepped up from generation levels (3.3,6.6,11,33kv) to over 39kv so that a huge amount of power can be transmitted over large distances.
  Transmitting at high voltage and lower current minimizes power losses over the distance
Commonly used transmission voltages are 69kv and 138kv, but there are also 44kv, 115kv, 161kv, 169kv, 230kv, and on large systems 345kv and 500kv. [13]
http://www.blackhillsenergy.com/services/programs/electric-system.php

## Slide 9: Transmission Substation
Fig 1.2: Basic Transmission Substation
Connects two or more transmission lines.
Disconnect switches on both the source and load sides permit isolation during maintenance or other periods when complete de-energization is required.

## Slide 10: Switching Substations
A switching substation is a combination of switching and controlling equipment arranged to provide circuit protection and system switching flexibility.
Operates at a single voltage.
More common on cooperative utilities transmission system.
Helps maintain reliable service under abnormal conditions.
Fig 1.3: Basic Switching Substation

## Slide 11: Substation configurations
Various factors affect the reliability of a substation/switchyard, one
of which is the arrangement of the buses and switching devices. In
addition to reliability, arrangements of the buses/switching device
will impact maintenance, protection, initial substation development
and cost [6].
Commonly used substation bus switching configurations include:
  Single Bus
  Double Bus, Double Breaker
  Main and Transfer Bus
  Double Bus, Single Breaker
  Ring Bus
  Breaker-and-a-Half

## Slide 12: Single Bus
Advantages:
Simple, low cost, only needs small land area
Disadvantages:
Least reliable arrangement
Failure to the main bus or of a circuit breaker causes an outage of the whole system
Connected line must be de-energized to perform maintenance to any device
Maintenance of the bus requires outage of entire system.
Figure 2.1
Involves one main bus, with all circuits connected directly to the bus

## Slide 13: Double Bus, Double Breaker
Advantages:
High reliability by having two breakers available for each circuit.
Maintenance of bus or circuit breaker may be done without interrupting circuits.
Flexible operating options as additional lines are added
Disadvantages:
High-cost because of additional breakers and larger land area requirement– usually only used at large generating stations.
Figure 2.2
Involves two main buses with two separate breakers for each circuit.

## Slide 14: Main and Transfer Bus
Advantages:
Reasonable cost, fairly small land area, easily expandable
If maintenance is required on circuit breaker, circuit can be fed from transfer bus while original breaker is isolated from system.
Disadvantages:
Moderate reliability since all circuits connected to the single main bus.
Additional circuit breaker needed for bus tie, complicates protection and relaying
Bus fault causes loss of entire substation.
Involves two separate and independent buses (main & transfer) with all circuits connected between the two. A bus tie breaker is connected between the buses.
Figure 2.3

## Slide 15: Double Bus, Single Breaker
Advantages:
Circuits may be operated from either bus by means of the switches.
In the event of breaker failure (as long as it’s not the bus tie) or bus fault, entire station isn’t shut down.
Disadvantages:
Additional circuit breakers needed, thus higher cost.
May cause interruption of non-faulted circuits.
Figure 2.4
Involves two main buses connected to each line circuit and a bus tie breaker– an extension of the single bus configuration.

## Slide 16: Ring Bus
Advantages:
High reliability and flexible operation
Circuit or bus failure only affects adjacent breakers, leaving the rest of the system energized.
Maintenance on a circuit breaker may be done without interrupting any circuit, including adjacent ones.
May be developed into a breaker-and-a-half scheme.
Disadvantages:
Breaker failure requires adjacent breakers to be tripped to isolate the fault.
Expansion of the ring is limited due to arrangement of circuits.
Figure 2.5
Involves breakers in a ring with circuits connected in between, creating a closed loop on the bus.

## Slide 17: Breaker-and-a-Half
Advantages:
High reliability, flexible operation, easily expandable
Any breaker can be removed without outage to any circuit
Fault on either bus can be isolated without interrupting service.
If center breaker fails, then two adjacent circuits lost, but if outside breaker fails, one circuit lost.
Disadvantages:
One-and-a-half breakers needed for each circuit means more cost and more land area needed
More complicated relaying
Figure 2.6
Involves two buses, and three circuit breakers for every 2 circuits.

## Slide 18: Comparison of configurations[6]
Configurations | Reliability | Relative Cost | Available Area
Single bus | Least– single failure can cause complete outage | Least– fewer components | Least– fewer components
Main & Transfer Bus | Least– same as Single Bus, but with flexibility in operating and maintenance | Moderate– fewer components | Least– fewer components
Double Bus, Single Breaker | Moderate– Depends on arrangement of bus components | Moderate– more components | Moderate– more components
Ring Bus | High– single failure isolates single component | Moderate– more components | Moderate– increases w/ number of circuits
Breaker-and-a-Half | High– single circuit failure isolates single circuit, bus failures don’t affect circuits | Moderate– 1.5 breakers for each circuit | Moderate– 1.5 breakers for each circuit
Double Bus, Double Breaker | High– single failure normally isolates single component | High– duplicated components | Great– more components per circuit

## Slide 19: Distribution Substation Devices
Transformer: Steps down voltage to level appropriate for distribution.
Transformer protection devices:
  Fuses: Stop the flow of current in the case of an internal fault or transformer short-circuit [13].
  Circuit breakers: Interrupt current
Switchgear: Combination of electrical disconnects, fuses, and circuit breakers used to isolate equipment. Used to de-energize equipment either for maintenance or to clear faults.

## Slide 20: Distribution Substation Devices
Voltage regulator: Raises or lowers distribution voltage to provide as close to constant voltage as possible.
Bypass switches: Provides means of taking devices in and out of service without de-energizing feeder circuits [9].

## Slide 21: Distribution Substation Devices
Circuit Breaker/ Recloser Bypass facilities: Able to interrupt fault current and disconnect faults from the system.
Reclosers: Can automatically restore a circuit when power is lost due to a temporary fault[10].

## Slide 22: Distribution Substation Devices
Surge Arrestors: Protect substation from voltage surges (ie. Damage during lightning storms), can be installed on power poles, towers, transformers, or circuit breakers, and diverts surges to the ground.
Shunt Capacitor Banks: Capacitors connected in parallel with lines. Supply reactive power to counteract the current being out-of-phase with voltage, which is introduced by inductive loads.

## Slide 23: Transmission Substation Devices
Transformer: Steps up voltage from generation levels to levels appropriate for transmission over long distances.
Circuit Breaker: Detects fault condition and interrupts to discontinue electrical flow, thus protecting the electrical circuit. Also used when needed to switch incoming or outgoing transmission circuits. [13]

## Slide 24: Transmission Substation Devices
Capacitor Banks: Capacitors connected in series or parallel.
  Capacitor: Stores electrical charge temporarily to help improve voltage regulation. Consists of two conducting surfaces separated by a nonconductor.
Disconnect switches/grounding switches: Provides isolation from incoming line.

## Slide 25: Transmission Substation Devices
Instrument transformers:
  When voltage or current is to large to be used by a device, instrument transformers scale it down. They are typically used by measurement, control, and protection devices.
  Current Transformer (CT), Potential Transformers (PT) (or, “Voltage Transformer”)
  Transducer: Converts one type of energy (electrical, mechanical, electromagnetic, chemical, acoustic, thermal) to another

## Slide 26: Transmission Substation Devices
Carrier equipment:
  Line traps: Connected in series with transmission line. Blocks high frequency carrier waves from entering station equipment, and lets power waves pass through.
  Capacitance Coupled Voltage Transformer (CCVT): Used in combination with Line traps to filter high frequency communication signals from the power frequency.

## Slide 27: Switching Substation Devices
Circuit Breaker: Detects fault condition and interrupts current to discontinue electrical flow, thus protecting the electrical circuit
Bypass switches: Provides means of taking devices in and out of service without de-energizing feeder circuits [9].

## Slide 28: Switching Substation Devices
Disconnect switches: Provides isolation from incoming lines.
Surge Arresters: Protect Substation from voltage surges

## Slide 29
Primary Power Lines
Ground Wire
Overhead Lines
Transformer for measurement of electric voltages
Disconnect Switch
Circuit Breaker
Current Transformer
Lightning Arrester
Main Transformer
Control Building
Security Fence
Secondary Power Lines
Substation Components

## Slide 30
Part 2: Substation Automation

## Slide 31: What is Substation Automation?
Substation automation may include traditional supervisory control and data acquisition (SCADA) equipment, but more often encompasses traditional SCADA functionality while providing extended monitoring and control capabilities through the use of non-traditional system elements.
Substation automation is the use of state-of-the-art computers, communications, and networking equipment to optimize substation operations and to facilitate remote monitoring and control of substations cost-effectively.
Substation automation uses intelligent electronic devices (IEDs) in the substation to provide enhanced integrated and coordinated monitoring and control capabilities.

## Slide 32: Automation and Substation
Substation Automation is really dependent on the interface between the substation and its associated equipment.
Necessary to have standard interface to all IED’s in a substation such that the communication capabilities of each may be merged
Interface should also serve the needs of corporate users to a level to justify its existence.
Five Levels of Substation Integration and Automation:
Utility Enterprise
Substation Automation Applications
IED Integration
IED implementation
Power System Equipment (transformers, breakers, …etc.)

## Slide 33: New Vs Existing Substations
New Substations
IEDs With Digital Communications
PLCs for Direct I/O
No Conventional RTUs
Existing Substations
May Integrate IEDs With Existing RTUs (Not Support Non-Operational and Remote Access Data Paths)
Integrate Existing RTU as IED or Eliminate Existing RTU and Use IEDs and PLCs for RTU I/O

## Slide 34: Communication Networks
The interface between the physical substation components and the virtual “automation” relies upon the communication infrastructure.
Types of Networks:
Wire Line Networks: Networks in which the medium of data transmission is physical ‘wire’.
      Point to point networks: dedicated link between two endpoints
      Point to multipoint networks: link between one and many
      Peer to peer networks: Any network node may share with any other node

## Slide 35: Communication Networks
Types of Networks (Continued)
Optical Fiber Systems: Information is transmitted via optical fibers.
    Fiber Loops: A setup where light can do many round trips in a fiber (Used to study long-length signals with limited fiber length)
    Fiber Stars: A setup where all end-points are connected through a single point.
    Ethernet over Fiber: The use of ethernet will increase in substations. Great for isolating devices and regions in the substations. There are media converters and fiber-ready routers, hubs, and switches readily available for these applications.
http://www.projectsmonitor.com/TELECOM/sterlite-targets-20-million-km-ofc

## Slide 36: Communication Networks
Communication network needs to be:
  High bandwidth (lots of data–& increasing in future), real-time monitoring
  Reliable (objective of no losses, deal with failure well)
  Scalable (allow for additional substations)
  Robust (performance doesn’t deteriorate under changing network traffic)
  Secure (safe from external attacks, transmitting sensitive information)
Internet Virtual Private Network (VPN) technologies allows minimum cost, highly reliable information sharing
  Good for substations in urban areas, but more difficult for rural substations where internet may not exist

## Slide 37: Communication Networks
Classes of communication technologies:
  Power Line: Uses existing electricity infrastructure to transmit data
    Advantages: Broad Coverage, High Bandwidth, Cost-Effective, Easy Installation
    Drawbacks: Lack of availability, Noise, High attenuation
  Satellite: Wide geographical coverage
    Advantages: Good for areas where other communication infrastructure may not exist, High Bandwidth
    Drawbacks: Long Delay (Comparatively higher than wired networks), Channel characteristics (Performance affected by weather or effect of fading)

## Slide 38: Communication Networks
Classes of communication technologies (Continued):
  Wireless: Transfer info without electrical conductors or wires
    Advantages: Relatively fast installation, lower cost (savings in cable costs)
    Disadvantages: Security concerns, bandwidth capacity limitations
  Optical Fiber: Information transferred via optical fibers
    Advantages: High capacity, immunity to Electro Magnetic Interference/ Radio Frequency Interference
    Disadvantages: Higher cost

## Slide 39: Communication Networks [11]
Hybrid Network:
  High speed communication core network (internet based VPN)
  Connection of rural substations to the high speed communication network via other means
    Power Line
    Satellite
    Wireless
    Optical fiber

## Slide 40: Functional diagram of SA system
1
2
3

## Slide 41: SA functional architecture
Includes:
SCADA system
Data Warehouse (Data Concentrator, SCADA interface, Router)
Three primary functional data paths:
  Operational data (instantaneous values of power system analog and status points– volts, circuit breaker status, …etc. ) to SCADA system
    Allows utility’s dispatchers to monitor and control power system
  Non-operational data(event summaries, records, …etc. ) to data warehouse
    Most challenging path due to characteristics and on-demand nature of data
  Remote access to IED.

## Slide 42: SA functional architecture
New vs. existing substations
  New substation typically has many IEDs for many functions with digital two-way communications, and no conventional remote terminal units (RTUs).
  Existing substations with RTU’s may:
    Integrate RTU with IED’s
    Integrate RTU as another IED
    Retire RTU and use IEDs and programmable logic controllers (PLC’s) instead

## Slide 43: SA Technical Issues [1]
System Responsibilities :
  The system must interface with all of the IEDs in the substation.
  The data from all the IEDs must be sent to the utility enterprise to populate the data warehouse or be sent to an appropriate location for storage of the substation data.
  The system must isolate supplier proprietary functionality by providing a generic interface to the IEDs.
  The system should be updated with a report-by-exception scheme, where status-point changes and analog-point changes are reported only when they exceed their significant dead band.

## Slide 44: SA Technical Issues Contd..
System Architecture
  The types of data and control that the system will be expected to facilitate are dependent on the choice of IEDs and devices in the system.
  This must be addressed on a substation-by-substation basis. The primary requirement is that the analog readings be obtained in a way that provides an accurate representation of their values .
Level 1 Field Devices
  Each electronic device (relay, meter, PLC, etc.) has internal memory to store some or all of the following data: analog values, status changes, sequence of events, and power quality.
  These data are typically stored in a FIFO (first in, first out) queue and vary in the number of events, etc., maintained.

## Slide 45: SA Technical Issues Contd..
Level 2 Substation Data Concentrator
  The substation data concentrator should poll each device for analog values and status changes at data collection rates consistent with the utility’s SCADA system.
  For example it should collect status points every 2 sec, tie-line and generator analogs every 2 sec, and remaining analog values every 2 to 10 sec).
  The substation data concentrator should maintain a local database.

## Slide 46: SA Technical Issues (Contd..)
Level 3 SCADA
  All data required for operational purposes should be communicated to the SCADA system via a communication link from the data concentrator.
  All data required for non-operational purposes should be communicated to the data warehouse via a communication link from the data concentrator.
  A data warehouse is necessary to support a mainframe or client-server architecture of data exchange between the system and corporate users over the corporate WAN (wide area network).

## Slide 47: SA Technical Issues (Contd..)
Substation host processor
  The substation host processor must be based on industry standards and strong networking ability, such as Ethernet, TCP/IP, UNIX, Windows 2000 or XP, Linux, etc.
  It must also support an open architecture, with no proprietary interfaces or products.
  An industry-accepted relational database (RDB) with structured query language (SQL) capability and enterprise-wide computing must be supported.

## Slide 48: SA Technical Issues (Contd..)
Substation LAN
  The substation LAN must meet industry standards to allow interoperability and the use of plug-and-play devices.
  Open-architecture principles should be followed, including the use of industry standard protocols (e.g., IEEE 802.x (Ethernet).
User Interface
  The user interface in the substation must be an intuitive design to ensure effective use of the system with minimal confusion.
  . An efficient display hierarchy will allow all essential activities to be performed from a few displays.

## Slide 49: Part 3: Evolution of SA

## Slide 50: Substation Communication
Supervisory Control and Data Acquisition (SCADA)
Centralized System controlling and monitoring a process (can be industrial, infrastructure, facility-based)

## Slide 51: Components of SCADA system
Human-Machine Interface (HMI)
  Presents to human operator all the processed data, allowing operator to monitor and control the processes.
Supervisory System
  acquires required data about a process and sending to the process control commands.
Remote Terminal Units (RTUs)
  Connect to sensors of process, help convert sensor signals to digital data
Programmable Logic Controller (PLCs)
  Used like field devices, versatile, configurable, economical, flexible
Communication infrastructure connecting RTUs to supervisory system.

## Slide 52: SCADA Communication Protocols
The standards process:
International Standards- ISO, IEC
National Standards– ANSI, NIST, IEEE
Proprietary Systems – vendor specific
Industry Practice- informal practice
Industry Standards- formalized practice

## Slide 53: SCADA Communication Protocols (Contd..)
DNP3
  Also known as Distributed Network Protocol, the DNP protocol was developed for communication with tele-control substations and other intelligent electronic devices (IEDs).
  Developed by GE Harris. Based on earlier parts of IEC 870-5.
  Originally, the protocol's main use was for slow serial communication, its present-day version also supports TCP/IP-based operation.
  DNP 3.0 commands a very powerful application layer, which allows the decoding of data without the use of implicit parameters.
  Application dominant in North America and industrialized Southern Hemisphere Countries.

## Slide 54: SCADA Communication Protocols (Contd..)
IEC 870-5
  Provides similar application facility as DNP.
  Developed by technical committee 57 working group 03 chartered to develop this standard.
  Primarily designed for point-to point or multi-drop serial link architectures but can also work over radio, LAN, etc.
  Unlike DNP, IEC 870-5 has no transport layer. Each data link frame containing application data is a complete application message.
  Application dominant in Europe and Middle East.

## Slide 55: SCADA Communication Protocols (Contd..)
UCA 1.0
  Also known as Utility Communication Architecture 1.0.
  This protocol arose from the need for common communication across the utility enterprise.
  The UCA 1.0 specification outlines a communication architecture based on existing international standards.
  It specifies the use of manufacturing message specification(MMS: ISO 19506) in the application layer for substation communication.

## Slide 56: SCADA Communication Protocols (Contd..)
ICCP [14]
  Also called as inter-control center communications protocol or IEC 60870-6 Tele control Application Service Element 2 (TASE.2) protocol.
  Developed by IEC TC57 WG07 for data exchange over Wide Area Networks (WANs) between a utility control center and other control centers, other utilities, power plants and substations.
  TASE.2 (ICCP) is used in almost every utility for inter-control center communications between SCADA and/or EMS systems. It is supported by most vendors of SCADA and EMS systems.

## Slide 57: SCADA Communication Protocols (Contd..)
UCA 2.0
UCA 2.0 is a next generation of UCA protocols and is a combination of ICCP protocols and Generic Object Models for Substation and feeder Equipment (GOMSFE) specification.
IEC 61850 has evolved from UCA 2.0 version.

## Slide 58: UCA and IEC 61850
Diagram shows the timeline and relation between UCA and IEC 61850 protocols

## Slide 59: SCADA Communication Protocols
IEC 61850
IEC 61850 is a superset of UCA 2.0, i.e. it contains almost all the UCA 2.0 specification and many other additional features.
IEC 61850 will provide interoperability between the IED’s for protection, control, monitoring, and automation in substations.
Chief advantages of IEC 61850 are:
  Simple substation structure: No more interface problems. With IEC 61850, protocol diversity and integration problems are no more a problem.
  Everything is simpler: Save time and costs on configuration, commissioning and maintenance.
  Reduction of costs: IEC 61850 replaces wiring between feeders, control switches, and signaling devices.
  More reliability: You only use one communication channel for all data – in real time, synchronized via Ethernet.

## Slide 60: Data Communications using 61850
Instead of dividing data into I/O types likes digital input data, analog input data, etc as is the case with DNP 3.0 , IEC 61850 divides the data into logical groupings such as protection data, switchgear data (shown in picture above)

## Slide 61: Communication Media
ARDIS (Advanced Radio Data Information Service)
  Originally developed jointly by Motorola and IBM in early 1980’s.
  ARDIS is optimized for short message applications that are relatively insensitive to the transmission delay.
  ARDIS uses connection oriented protocols well suited for host/terminal applications.
  As a radio based service, ARDIS can be expected to be immune to most of the Electromagnetic Compatibility (EMC) issues associated with substations.
  Provides 4800 –bps or 19.2 kbps service using 25 kHz channel in the 800 MHz band.

## Slide 62: Communication Media
Plain Old Telephone Service (POTS)
Standard 2-wire analog telephone lines known as plain old telephone service (POTS) in the telecommunication industry.
Probably the most economical way to communicate with remote locations in situations where only occasional data transfer is required.
Installation of dial modem is very straight forward and plenty of off-the shelf components are available giving users plenty of options.
Not suitable for transferring large amounts of data since the data rates for modems are limited to 33kbps and below.
GPR concerns can limit the POTS use.

## Slide 63: Communication Media
Wireless Telephone Service
Wireless telephone service is useful where GPR concerns prevent the installation prevent the installation of POTS line.
The biggest difference will be a degradation in performance when compared to POTS since the bandwidth available on a cellular or PCS connection will limit data rates to a maximum of 14.4 kbps.
Wireless service is generally priced on flat rate basis with per minute charges.
Packages that include a large number of minutes per month can make cellular access to a substation affordable, especially when a connection is only needed a few times per week or less.

## Slide 64: Communication Media
Cellular Digital Packet Data (CDPD)
In addition to regular wireless telephone service, some cellular service providers offer a service known as CDPD.
CDPD is internet based technology(TCP/IP) that allows the transmission of data on idle cellular channels.
Requires the use of special CDPD radios.
The service is best suited for applications that send bursts of data on an occasional basis, as it is priced on a per-kilobyte basis.
CDPD is generally only available in large metropolitan areas and in most cases only offered by a single wireless service provider in a given area which limits competition and keeps the prices high.

## Slide 65: Communication Media
Telephone Lines : leased and dial-up
Useful where POTS line is acceptable but continuous access to the substation is desired.
Dedicated lines or leased or private voice –grade lines with standard 3-kHz voice bandwidth can be provided by telephone company.
There are some security issues for all telephone circuits that they can be easily tapped in an obtrusive manner which makes them vulnerable to security attacks.
Some security measures could be enabling sign-on passwords with dial-back modem or physical layer encryption.

## Slide 66: Communication Media
Private Microwave Radio
Many utilities have built their own networks by utilizing high-capacity microwave radio systems. These systems are owned and operated by the utilities
Depending on the radio type, can transmit data anywhere from 1.5 Mbps (24 voice channels) to hundreds of Mbps (thousands of voice channels).
The cost of ownership of a microwave system, however, can be quite high.
Microwave radios require line-of-site transmission and therefore often require tall (100-300 ft.) towers to allow for effective communication

## Slide 67: Communication Media
Multiple Address Systems (MAS)
Multiple Address Systems (MAS) are 900 MJ3z radio systems designed for SCADA applications.
They operate in a point-to-multipoint mode where a “master” radio station polls “slave” radios located at the substations.
MAS stations typically operate at 9.6 kbps and do not require twisted pair circuits in the substation.
Slow MAS speed limits the number of polls the performed per minute, meaning utility must limit the number of substations its serving with a single MAS.
MAS is a popular communication system used by utilities for SCADA and Distribution Automation (DA) systems.

## Slide 68: Communication Media
Very Small Aperture Terminal Satellite(VSAT):
VSAT services are specifically tailored towards SCADA applications.
These services utilize a dish approximately 18-24 inches in diameter and are offered by service providers who handle issues such as collection of data and leasing of satellite time.
VSAT systems are especially suited for remote locations that would require expensive leased lies or are otherwise unreachable.
VSAT service providers generally charge a per month charge in the range one or two hundred dollars per month with a per-Mb charge for the data.

## Slide 69: Communication Media
Land-Mobile Two-Way Radio
For applications that transmit small amounts of data, traditional two-way radio systems may be able to support communication.
Applications suited for two-way radio include report-by-exception alarms (i.e. simple contact closures) or simple telemetry such as the report of a river level every minute or two.
The biggest drawback to two-way radio is probably its relatively low speed and short range.
Data rates are usually 9.6 kbps or less, although some dedicated links can run as fast as 19200 bps.
Two-way radio is usually considered when a low cost solution is needed for transmitting low-speed data a short distance (10 miles or less)

## Slide 70: Communication Media
Optical Fiber
The most versatile technology of substation communication.
Optical fiber have the capability of operating at extremely high data rates.
A wide variety of applications (not only telecommunications but also protective relaying and measurement systems) have been adapted to work over optical media.
Optical Fiber does not conduct electricity and hence its very safe from GPR perspective.
Fiber optic systems can be obtained that can transfer data anywhere from 1.5 Mbps (24 voice channels) to almost 10 Gbps (well over 100,000 voice channels).
The fiber optic cable itself is quite expensive to install but the enormous capacity makes it possible for utilities to share capacity with outside parties, which helps recover the cost of installation.

## Slide 71: Communication Media
Power-Line Carrier (PLC)
PLC systems operating on narrow channels between 30 and 500kHz are frequently used for high-voltage line protective relaying applications.
Typically one station sends a signal to trip a relay in another station by using simple one-bit messages using either amplitude or frequency shift keying.
Some PLC systems have also been developed for specialized distribution feeder applications such as remote meter reading and distribution automation.
The TWACS (Two-Way Automatic Communication System) is one such PLC system used for both meter reading and distribution automation.

## Slide 72: Communication Media
Short Message System (SMS)
Also known as text messaging uses forward and reverse control channels of cell phone systems to provide two-way communication for very short telemetry messages.
Well suited for control and status messaging from simple remote terminal units (RTUs).
Utility interface to the system is provided using internet , telephone and pager services.

## Slide 73: Important Standards
IEEE 802.x Networking Standards
IEEE Electromagnetic Interference (EMI) Standards
IEC 870-5 Standards
DNP3 specifications
IEC 870-6 TASE.2 (UCA/ICCP) Standards
IEC 61850/UCA Standards
ISO Reference Models

## Slide 74: Part 4: SA and Cyber Security

## Slide 75: Cyber Security Terminology
Cyber Security: Security from threats conveyed by computer or computer terminals, also the protection of other physical assets from modification or damage from accidental r malicious misuse of computer based control facilities.
Default password: A password is a sequence of characters that one must input to gain access to a file, application or computer system.

## Slide 76: Cyber Security Terminology (Contd..)
DNP3: Distributed networks protocol, a non-proprietary communications protocol designed to optimize the transmission of data acquisition information and control commands from one computer to another.
Firewall: A device that implements security policies to keep a network safe from unwanted data traffic

## Slide 77: Cyber Security Terminology (Contd..)
Protocol: A formal set of conventions governing the relative timing of message exchange between two communication terminals.
RTU: Remote terminal unit, the entire complement of devices, functional modules, and assemblies that are electrically interconnected to effect the remote station supervisory functions. The equipment includes the interface with the communication channel but doesnot include the interconnecting channel.
Remote access: Access to the control system or IED by a user whose operation terminal is not directly connected to the control system or IED.

## Slide 78: General Cyber Security Concerns
Some examples are :
  Relay Settings : They are often accessed by protection engineers to update and change the settings values.
  Insecure communications media: The data messages that substation IEDs exchange with the outside world are often transmitted over media that are potentially open to eavesdropping or active intrusion.
  Open Protocols: The communication protocols most frequently used in substations are very well known.
  Lack of authentication: Communication protocols in current use do not provide a secure means for systems that exchange data to authenticate each other’s identity.

## Slide 79: References
http://www.electricenergyonline.com/?page=show_article&mag=43&article=321
A.P Apostolov, “ Configuration Requirements for UCA based IEDs for Protection and Control,” CIGRE 2001 SC 34 Colloquium, Sibiu, Sept. 2001
http://www.ece.iit.edu/~flueck/chicago_pes/2002/SA_Fund_BestPractices.pdf
http://www.atrakenergy.com/Resources/PSC-2004.pdf
www.ee.iastate.edu/~jdm/ee653/SubstationReliability.pdf
http://www.csanyigroup.com/air-insulated-substations-bus-switching-configurations
http://www.powertransformer.us/substationtransformers.htm
McDonald, J.D.; , "Substation automation. IED integration and availability of information," Power and Energy Magazine, IEEE , vol.1, no.2, pp. 22- 31, Mar/Apr 2003 doi: 10.1109/MPAE.2003.1192023 URL: http://ieeexplore.ieee.org/stamp/stamp.jsp?tp=&arnumber=1192023&isnumber=26717

## Slide 80: References (Contd..)
[9] http://www.transmission-line.net/2011/04/type-of-switches-on-transmission-and.html
[10] http://www.oncor.com/community/knowledgecollege/energy_library/pathway/pathways_distribution.aspx
[11] http://www.ece.gatech.edu/research/labs/bwn/substation/description.html
[12] Qureshi, M.; Raza, A.; Kumar, D.; Sang-Sig Kim; Un-Sig Song; Min-Woo Park; Hyuk-Soo Jang; Hyo-Sik Yang; Byung-Seok Park; , "A survey of communication network paradigms for substation automation," Power Line Communications and Its Applications, 2008. ISPLC 2008. IEEE International Symposium on , vol., no., pp.310-315, 2-4 April 2008 doi: 10.1109/ISPLC.2008.4510445 URL: http://ieeexplore.ieee.org/stamp/stamp.jsp?tp=&arnumber=4510445&isnumber=4510387 [13] http://smud.apogee.net/foe/
[14] http://intelligrid.epri.com/architecture/New_Technologies/Tech_IEC_60870-6_(ICCP).htm

## Slide 81: Module 5 Concluding Comments
1
2
3
4