## Slide 1: GridLAB-D: A Unique Tool to Design a Smarter Grid
Jason Fuller
Electricity Infrastructure Technical Group Manager
Pacific Northwest National Laboratory

## Slide 2: GridLAB-D: A Unique Tool to Design a Smarter Grid
Open-source, time-series simulation of an operating smart grid, from the substation to individual end-use loads & distributed energy resources, in unprecedented detail
Simultaneously solves
Smart grid analyses
  field projects
  technologies
  control strategies
  cost/benefits
Time scale: ms to years
Open source (BSD-style)
Contributions from
  government
  industry
  academia
Vendors can add or extract own modules
Over 80,000 downloads in over 150 countries
Power Systems
Loads & DERs
DSO Markets
Unifies models of the key elements of a smart grid:
1) power flow 2) control systems
3) retail markets 4) electromechanical dynamics
5) end-use load behavior in tens of thousands of buildings and devices

## Slide 3: GridLAB-D Capabilities
Typical Use Cases
Interconnection of distributed generation and storage
New and innovative retail market structures (e.g., DSOs)
Evaluation of demand response and energy efficiency
Volt-VAr optimization and conservation voltage reduction design
Sectionalizing, reconfiguration, automation, and restoration
Microgrids and resiliency
Performs time-series simulations
  Seasonal effects (days to years)
  Midterm dynamic behavior (secs to hrs)
  System dynamics (milliseconds)
Simulates control system interactions
  Device- and system-level controls
  Market interactions

## Slide 4: Definitions for this presentation
What does agent-based mean?
  The changing states of individual devices/agents are modeled independently
  The interactions between individuals are captured
  The environment in which these evolve together is a combination of all these interactions
Dynamic simulation can include time series (timestep greater than 1 second)
For this presentation, quasi-steady state simulation is defined as having a timestep at 1 second or greater
  Sequence of powerflow states coupling other behaviors, such as multi-state load models
  Focused typically on 1-minute or longer range – behavioral and diurnal dynamics
For this presentation, dynamic simulation is defined as having a timestep less than 1 second
  Sequence of powerflow states coupling differential equations
  Focused mainly on 0.5 ms to 50 ms range – electromechanical dynamics

## Slide 5: GridLAB-D Studies (General)
American Reinvestment and Recovery Act (ARRA) Smart Grid Investment Grant (SGIG) evaluation
  Taxonomy-feeder based
  Several technologies examined
Conservation Voltage Reduction/Volt-Var Control evaluations
  Validated against actual system data
  Developed methods for estimating CVR/VVO impacts
Business case for scalable demand response
  Evaluated cost reductions and help refine the implementation
Evaluate solar carrying capacity and installation impacts
  Examined feeder-level impacts of solar deployments
Compare the cost-to-benefits ratio of household types or green- vs. brown-field growth.
Volt-Var Control evaluation

## Slide 6: Dynamic Simulation Usages
Transients on distribution systems
  Tripping of IEEE 1547A devices
  Grid Friendly Appliance™ impacts
Microgrid Analysis – Resiliency
  Inrush and line charging
    Overhead and underground lines being energized
    Transformer saturation
    Motor starting surges
  Frequency and voltage impacts
    Acceptable ranges
    Secondary tripping of items
  Evaluate methods for improving resiliency
WSU example for evaluating “Microgrids as a Resiliency Resource”
Transformer current in 8500-node system
during connection of primary transformer

## Slide 7: How does GridLAB-D Work?

## Slide 8: GridLAB-D Architecture
Core responsibilities
Integrates models
Manages memory & CPUs
Coordinates time
Handles stochastic requirements
Synchronizes updates (ranks)
Coordinates variable sharing
Manages convergence
Tracks numerical stability
Measures system performance
Debugs module behavior
GridLAB
Core
Weather
Power System
Communications
Controls
Telemetry
Behavior
Markets
Events
Buildings
Analysis
Protection

## Slide 9: Defining the System
Module
Collects classes that are related
Groups common parameters and solvers
May be proprietary or open-source
Class
Defines similar objects
Properties are the same for all objects, but set parametrically
Static classes are pre-compiled in distribution
Object
Instances of classes
Used to define the different agents in the system
Each property is assigned an individualized value

## Slide 10: Example Instantiation of an Object
Set a house with default values
  module residential; // module declaration
  object house { // instantiation of an object of class house
  name MyHouse;
  }
Set a house with custom values
  module residential; // module declaration
  #include "CA-Los_angeles.glm“ // define weather conditions
  object house {
  floor_area random.normal(1500,300) sf; // set properties
  heating_setpoint 70.0 degF;
  cooling_setpoint 76.0 degF;
  thermostat_deadband 1.0 degF;
  }

## Slide 11: Running a Simulation

## Slide 12: Creating a GridLAB-D Model (GLM) file
Instantiates the model to be loaded into the solver
Defines the initial conditions of each agent
Defines the relationships between the agents
Sets the run-time
Defines which parameters to observe
Text-based!
  clock {
  timezone PST+8PDT;
  starttime '2000-01-01 0:00:00'; //defines a 6-month
  stoptime '2000-07-01 0:00:00'; //simulation length
  }
  module powerflow;
  module residential;
  module tape;
  object triplex_meter {
  phases AS;
  nominal_voltage 120 V;
  name my_meter1;
  }
  object house {
  parent my_meter1;
  name my_house1;
  floor_area random.normal(1500,300) sf;
  heating_setpoint 70.0 degF;
  }
  object recorder{
  parent my_house1;
  property air_temperature,heating_setpoint;
  file theat_record.csv;
  interval 60 s;
  }

## Slide 13: Running the Model
To execute, you get to use a command prompt!! (and the equivalent in Linux and MacOS)

## Slide 14: Outputs
Must be defined
  Does NOT automatically record every variable at every timestep
Typically CSVs
  Most often a time series of data channels
  Some aggregation and reporting
  Can also be pushed to databases (or external connections)
XML “dump” can be used to pull the entire system state simultaneously
Collectors can aggregate similar properties from across many agents
Note: I added a couple metering points and added a climate object.

## Slide 15: Input Parameters
Fixed, static parameters
Randomized over a population
Driven by a time-series input
  Player
  Shape
  Schedule
  External Source
Once properly randomized (and diversified), we can build a load shape most of us are more familiar with…

## Slide 16: Example of Adding Agents
1 Home
8 Homes
100 Homes
Loadshape

## Slide 17: Why do we want to model as agents?
Simple examples of interactions
  Resistive Heating
  Heat Pump HVACs
The interactions of the different agents (and particularly their controls) can often reveal unforeseen behaviors

## Slide 18: Getting the Diversity can be Challenging
  clock {
  timezone PST+8PDT;
  starttime '2000-01-01 0:00:00';
  stoptime '2000-07-01 0:00:00';
  }
  module powerflow;
  module residential;
  module tape;
  object triplex_meter {
  phases AS;
  nominal_voltage 120 V;
  name my_meter1;
  }
  object house {
  parent my_meter1;
  name my_house1;
  floor_area random.normal(1500,300);
  heating_setpoint 70.0 degF;
  }
  object recorder{
  parent my_house1;
  property air_temperature;
  file theat_record.csv;
  interval 60 s;
  }

## Slide 19: We try to help…
Model creation, conversion, and execution scripts are available
  A number are available on GridLAB-D repository (primarily Python)
  Some are located in other open-source tools (e.g., TESP, OMF, etc.)
“Prototypical” and IEEE circuits are available
  24 prototypical circuits are converted utility circuits that are regionalized to North America
  These can act as starting points, rather than starting from scratch

## Slide 20: Once we have a model, what are we looking for?
Transient Events
Diurnal Cycles
Seasonal/Annual Variations
Population Distributions
Time-Dependent Behaviors
Improving Controls
(Unintended Interactions)

## Slide 21: Further Information
Contact:
Jason Fuller
jason.fuller@pnnl.gov
Frank Tuffner
francis.tuffner@pnnl.gov
Video Tutorials, Walkthrough, and Other Good Information
https://www.gridlabd.org/started.stm
GitHub Links
https://github.com/gridlab-d/gridlab-d
Wiki
http://gridlab-d.shoutwiki.com/wiki/Main_Page
SourceForge Forums (Help Questions)
https://sourceforge.net/p/gridlab-d/discussion
Users’ Publications
http://gridlab-d.shoutwiki.com/wiki/Publications