## Slide 1: Substation and Distribution Automation Module 2
Three Phase Transformer Models
Center –Tapped Transformers and Secondaries
IEEE Test Systems

## Slide 2: Module 1 Overview
Part 1: Overhead Lines
Part 2: Underground lines
Part 3: Three Phase Transformer Models
Part 4: Center –Tapped Transformers and Secondaries
Part 5: IEEE Test Systems

## Slide 3: Part 3: Three Phase Transformer Models
Three Phase Transformer Models
  General Three Phase Transformer Banks
  Generalized Matrices
  Symmetrical Components
  The Delta-Grounded Wye Step Down Connection
  The Ungrounded Wye-Delta Step Down Connection
  The Grounded Wye-Grounded Wye Connection
  The Delta-Delta Connection
  Open Wye-Open Delta
  Thevenin Equivalent Circuit

## Slide 4
    Three-phase transformer banks in the distribution substation transform the transmission or sub-transmission level voltages to the distribution feeder level voltage.
    Different substations transformer connections exist, like the Delta-grounded wye, the delta-delta transformer,… etc.
    The connection used depends on the configuration of the distribution feeder.
  Three Phase Transformer Models

## Slide 5
    Three-phase transformer banks on the feeder will provide the final voltage transformation to the customer’s load.
    Again, different transformer connections can be applied depending on the load characteristics (whether a pure 3 phase load or a combination of single phase and three phase loads).
  Three Phase Transformer Models

## Slide 6
  Quick Review of Wye and Delta Connection
    Figure 1.0: Wye and delta source connections
    Figure 2.0: The line-neutral voltages in terms of the line-line voltages

## Slide 7
    If all the voltages are considered to be positive sequence components (to be discussed later), can be related to as
        (1)
    The reverse relationship also works.
(2)
  Quick Review of Wye and Delta Connection

## Slide 8
  Quick Review of Wye and Delta Connection
    If the voltages considered are negative sequence components (to be discussed later), and can be related as:
(3)
        and
(4)
    The relationship can also be understood by the following.
      (Let )
    (5)
    (6)
    (7)

## Slide 9: Part 3: Three Phase Transformer Models
Three Phase Transformer Models
  General Three Phase Transformer Banks
  Generalized Matrices
  Symmetrical Components
  The Delta-Grounded Wye Step Down Connection
  The Ungrounded Wye-Delta Step Down Connection
  The Grounded Wye-Grounded Wye Connection
  The Delta-Delta Connection
  Open Wye-Open Delta
  Thevenin Equivalent Circuit

## Slide 10
        General Three Phase Transformer Banks
    Figure 3.0 defines the various voltages and currents of all transformer banks with source side ‘’ and load side ‘’.
    The notation is such that upper-case letters refer to the source side and lower-case letters refer to the load side of the bank
  Three Phase Transformer Models
Step-Down Connection:
leads by 30 degrees
leads by 30 degrees
Step-Up Connection:
leads by 30 degrees
leads by 30 degrees
Figure 3.0

## Slide 11
        Generalized Matrices
    The matrix equations for computing the voltages and currents at node as a function of the voltages and currents at node are given by:
(8)
(9)
    The voltages at node as a function of the voltages at node and the currents at node are given by:
    (10)
  Three Phase Transformer Models

## Slide 12: Part 3: Three Phase Transformer Models
Three Phase Transformer Models
  General Three Phase Transformer Banks
  Generalized Matrices
  Symmetrical Components
  The Delta-Grounded Wye Step Down Connection
  The Ungrounded Wye-Delta Step Down Connection
  The Grounded Wye-Grounded Wye Connection
  The Delta-Delta Connection
  Open Wye-Open Delta
  Thevenin Equivalent Circuit

## Slide 13
        Generalized Matrices
    Equation (10) will be used in the forward back sweep method to be described later.
    The matrices and represent the line-to-neutral voltages for an ungrounded wye connection or the line-to-ground voltages for a grounded wye connection.
    For a delta connection, the voltage matrices represent “equivalent” line-to-neutral voltages.
    The current matrices represent the line currents regardless of the transformer winding connection.
  Three Phase Transformer Models

## Slide 14: Part 3: Three Phase Transformer Models
Three Phase Transformer Models
  General Three Phase Transformer Banks
  Generalized Matrices
  Symmetrical Components
  The Delta-Grounded Wye Step Down Connection
  The Ungrounded Wye-Delta Step Down Connection
  The Grounded Wye-Grounded Wye Connection
  The Delta-Delta Connection
  Open Wye-Open Delta
  Thevenin Equivalent Circuit

## Slide 15
    Unbalanced systems cannot be studied in terms of balanced three phase voltages and currents
    Hence the method of symmetrical components is used for unbalanced systems
If the original phasors are voltages, they may be designated Va, Vb, and Vc. The three sets of symmetrical components are designated by the additional subscript 1 for the positive-sequence components, 2 for the negative-sequence components, and 0 for the zero-sequence components
  Quick Review – Symmetrical Components

## Slide 16
    The positive-sequence components of Va, Vb, and Vc are Va1, Vb1, and Vc1, respectively. Similarly, the negative-sequence components are Va2, Vb2, and Vc2, and the zero-sequence components are Va0, Vb0, and Vc0, respectively
Va1
Vc1
Vb1
Va2
Vc2
Vb2
Va0 = Vb0 = Vc0
Positive-sequence
components
Negative-sequence
components
Zero-sequence
components
Fig: Three sets of balanced phasors which are the symmetrical components of three unbalanced phasors
  Quick Review – Symmetrical Components

## Slide 17
Since each of the original unbalanced phasors is the sum of its
components, the original phasors expressed in terms of their components are
The number of unknown quantities can be reduced by expressing
each component of Vb and Vc as the product of Va and some function of the operator
  Quick Review – Symmetrical Components

## Slide 18
  Quick Review – Symmetrical Components
Symmetrical component equations for voltages
matrix form
where

## Slide 19
  Quick Review – Symmetrical Components
Which shows us how to solve three unsymmetrical phasors into their symmetrical components
Similar results apply to line-to-line voltages by replacing Vab, Vbc, and Vca in the above equations

## Slide 20
        Transformers that will be modeled in the coming slides……
        1. The Delta-Grounded Wye Step Down Connection
    Typically used in a distribution substation serving a four-wire wye feeder system.
    Another application is to provide service to a load that is primarily single-phase, since three single-phase circuits are available.
        2. The Ungrounded Wye Delta Connection
    Typically used to provide service to a combination of single-phase “lighting” load and three-phase “power” load such as an induction motor.
  Three Phase Transformer Models

## Slide 21
        Transformers that will be modeled in the coming slides……
  3. The Grounded Wye-Grounded Wye Connection
Primarily used to supply single-phase and three-phase loads on four-wire multigrounded systems.
  4. The Delta-Delta Connection
Primarily used on three-wire delta systems to provide service to a three-phase load or a combination of three-phase and single-phase loads.
  5. Open Wye-Open Delta
Another connection used to supply a combination of single-phase and three-phase loads. Commonly used when the three-phase load is small compared to the single-phase load.
  Three Phase Transformer Models

## Slide 22: Part 3: Three Phase Transformer Models
Three Phase Transformer Models
  General Three Phase Transformer Banks
  Generalized Matrices
  Symmetrical Components
  The Delta-Grounded Wye Step Down Connection
  The Ungrounded Wye-Delta Step Down Connection
  The Grounded Wye-Grounded Wye Connection
  The Delta-Delta Connection
  Open Wye-Open Delta
  Thevenin Equivalent Circuit

## Slide 23
        The Delta-Grounded Wye Step Down Connection
    Typically used in a distribution substation serving a four-wire wye feeder system.
    Another application is to provide service to a load that is primarily single-phase.
    Because of the wye connection, three single-phase circuits are available, making it possible to balance the single phase loading on the transformer bank.
  Three Phase Transformer Models

## Slide 24
        The Delta-Grounded Wye Step Down Connection
  Three Phase Transformer Models
Figure 4.0

## Slide 25
        The Delta-Grounded Wye Step Down Connection
    With reference to Figure 4.0, the line-to-line voltages on the primary side of the transformer connection as a function of the ideal secondary side voltages is:
      (13)
    where is the turns ratio defined as (12)
  Three Phase Transformer Models

## Slide 26
        The Delta-Grounded Wye Step Down Connection
    In condensed form, (13) is
    (14)
    where
    (15)
    To get the line-to-neutral voltages from the line-to-line voltages, we apply the theory of symmetrical components.
  Three Phase Transformer Models

## Slide 27
        The Delta-Grounded Wye Step Down Connection
    The known line-to-line voltages are transformed to their sequence voltages by:
  Three Phase Transformer Models
(16)
where
(17)

## Slide 28
        The Delta-Grounded Wye Step Down Connection
    By definition the zero sequence line-to-line voltage is always zero.
    The relationship between the positive sequence and negative sequence line-to-neutral and line-to-line voltages in matrix form is
    (18)
    (19)
    where (20)
  Three Phase Transformer Models

## Slide 29
        The Delta-Grounded Wye Step Down Connection
    Since the zero sequence line-to-line voltages is zero, the (1,1) term of can be taken as 1.0.
    Knowing the sequence line-to-neutral voltages, the equivalent line-to-neutral voltages can be determined.
    The equivalent line-to-neutral voltages, as a function of the sequence line-to-neutral voltages, are
    (21)
    Substitute equation (19) into equation (21):
    (22)
  Three Phase Transformer Models

## Slide 30
        The Delta-Grounded Wye Step Down Connection
    Substitute equation (16) into equation (22):
    (23)
  where (24)
    Equation (24) provides a method for computing the equivalent line-to-neutral voltages from knowledge of line-to-line voltages.
  Three Phase Transformer Models

## Slide 31
        The Delta-Grounded Wye Step Down Connection
    Equation (14) can now be substituted into equation (24).
    (25)
    where (26)
    Equation (26) defines the generalized matrix for the delta-grounded wye step-down connection.
  Three Phase Transformer Models

## Slide 32
        The Delta-Grounded Wye Step Down Connection
    The ideal secondary voltages as a function of the secondary line-to-ground voltages and the secondary line currents are:
    (27)
    where (28)
  Three Phase Transformer Models

## Slide 33
  Three Phase Transformer Models
        The Delta-Grounded Wye Step Down Connection
    Substitute equation (27) into equation (25).
  (29)
      where
  (30)

## Slide 34
        The Delta-Grounded Wye Step Down Connection
    For the generalized and matrices, we solve equation (14) for the ideal secondary voltages.
      (31)
    The line-to-line voltages as a function of the equivalent line-to-neutral voltages are:
    (32)
    where (33)
  Three Phase Transformer Models

## Slide 35
    Substituting equation (32) into equation (31) we get:
    (34)
    where (35)
    Substitute equations (27) into equation (34)
    (36)
  Three Phase Transformer Models
        The Delta-Grounded Wye Step Down Connection

## Slide 36
        The Delta-Grounded Wye Step Down Connection
    Rearrange equation (36).
    (37)
    where (38)
    Equations (29) and (37) are the generalized voltage equations for the step-down delta-grounded wye transformer.
  Three Phase Transformer Models

## Slide 37
        The Delta-Grounded Wye Step Down Connection
    For currents, the thirty degree connection specifies that the positive sequence current entering H1 terminal will lead the positive sequence currents leaving the X1 terminal by 30 degrees.
    Figure 5.0 shows the currents of the delta-grounded wye step down connection
  Three Phase Transformer Models
Figure 5.0

## Slide 38
        The Delta-Grounded Wye Step Down Connection
    Applying Kirchhoff’s Current Law (KCL):
    (38)
    (39)
    The matrix equation relating the delta primary currents to the secondary line currents is given by:
    (40)
    (41)
  Three Phase Transformer Models

## Slide 39
        The Delta-Grounded Wye Step Down Connection
    Substitute equation (41) into equation (40).
    (42)
    where (43)
    (44)
    Equation (42) provides a direct method of computing the phase line currents at node knowing the phase line currents at node .
  Three Phase Transformer Models

## Slide 40
        The Delta-Grounded Wye Step Down Connection
    The equations derived here were for the step down connection.
    The procedure for the step up connection will be the same, except the connection between the transformer windings will be different, as will be the definition of the generalized matrices.
  Three Phase Transformer Models

## Slide 41: Part 3: Three Phase Transformer Models
Three Phase Transformer Models
  General Three Phase Transformer Banks
  Generalized Matrices
  Symmetrical Components
  The Delta-Grounded Wye Step Down Connection
  The Ungrounded Wye-Delta Step Down Connection
  The Grounded Wye-Grounded Wye Connection
  The Delta-Delta Connection
  Open Wye-Open Delta
  Thevenin Equivalent Circuit

## Slide 42
        The Ungrounded Wye-Delta Step Down Connection
  Three Phase Transformer Models
    Three single-phase transformers can be connected in a wye-delta connection and the neutral of the wye can be grounded or ungrounded.
    The grounded wye is rarely used because:
      The grounded wye provides a path for the zero sequence currents for line-to-ground faults upstream from the transformer bank and can cause the transformers to be susceptible to burnouts.
      If one phase of the primary circuit is opened, the transformer bank will continue to provide a three phase service, however the remaining two transformers may be subject to overload.
    Thus, the ungrounded wye-delta connection is used to provide service to a combination of single-phase “lighting” load and a three-phase “power” load such as an induction motor.

## Slide 43
        The Ungrounded Wye-Delta Step Down Connection
  Three Phase Transformer Models
Figure 6.0

## Slide 44
    The basic ideal transformer voltage and current equations as a function of the turns ratio are:
        The Ungrounded Wye-Delta Step Down Connection
  Three Phase Transformer Models
Figure 7.0
      where (45)

## Slide 45
      (46)
      (47)
      (48)
        The Ungrounded Wye-Delta Step Down Connection
  Three Phase Transformer Models
    The basic ideal transformer voltage and current equations as a function of the turns ratio (continued):

## Slide 46
      The line-to-line voltages at node as a function of the ideal transformer voltages and the delta currents are given by:
      (50)
      (51)
  Three Phase Transformer Models
        The Ungrounded Wye-Delta Step Down Connection
      Solve equation (46) for the ideal delta transformer voltages.
        (49)

## Slide 47
        The Ungrounded Wye-Delta Step Down Connection
      Substitute equation (48) and equation (49) into equation (51).
        (52)
  where
  (53)
  Three Phase Transformer Models

## Slide 48
        The Ungrounded Wye-Delta Step Down Connection
      The line currents on the delta side of the transformer bank as a function of the wye transformer currents are given by:
    (54)
    where (55)
  Three Phase Transformer Models

## Slide 49
      Substitute equation (48) into equation (54).
      (56)
      where (57)
  Three Phase Transformer Models
        The Ungrounded Wye-Delta Step Down Connection

## Slide 50
        The Ungrounded Wye-Delta Step Down Connection
      Because the matrix is singular, it is not possible to use equation (56) to develop an equation relating the wye side line currents at node to the delta side line currents at node .
      Hence three independent equations must be written.
        Two equations are based on the KCL at the 2 vertices of the delta connection.
        The third is from the sum of the three delta currents (which will equal zero as the wye connection is ungrounded, and hence all currents on the wye side will equal zero).
  Three Phase Transformer Models

## Slide 51
        The Ungrounded Wye-Delta Step Down Connection
      Hence, the three independent equations in matrix form are given by:
(58)
      Solve equation (58) for the delta currents.
      (59)
      (60)
  Three Phase Transformer Models

## Slide 52
        The Ungrounded Wye-Delta Step Down Connection
      Equation (60) can be modified to include the phase current by setting the third column of the matrix to zero:
      (61)
      (62)
  Three Phase Transformer Models

## Slide 53
        The Ungrounded Wye-Delta Step Down Connection
      Solve equation (48) for and substitute into equation (62).
      (63)
      where (64)
      Equation (64) defines the generalized constant matrix for the ungrounded wye-delta transformer connection.
  Three Phase Transformer Models

## Slide 54
        The Ungrounded Wye-Delta Step Down Connection
      The generalized matrices and can now be developed.
      Solving equation (52) for :
      (65)
      Substitute equation (63) into equation (65):
(66)
  Three Phase Transformer Models

## Slide 55
        The Ungrounded Wye-Delta Step Down Connection
      But,
        (67)
        where (68)
        (69)
  Three Phase Transformer Models

## Slide 56
  Three Phase Transformer Models
        The Ungrounded Wye-Delta Step Down Connection
      The generalized constant matrices have been developed for computing the voltages from the load to the source.
      The reverse generalized matrices can be developed by substituting equation (52) into equation (23):
(70)

## Slide 57
  Three Phase Transformer Models
        The Ungrounded Wye-Delta Step Down Connection
where (71)
(72)

## Slide 58: Part 3: Three Phase Transformer Models
Three Phase Transformer Models
  General Three Phase Transformer Banks
  Generalized Matrices
  Symmetrical Components
  The Delta-Grounded Wye Step Down Connection
  The Ungrounded Wye-Delta Step Down Connection
  The Grounded Wye-Grounded Wye Connection
  The Delta-Delta Connection
  Open Wye-Open Delta
  Thevenin Equivalent Circuit

## Slide 59
        The Grounded Wye-Grounded Wye Connection
    The grounded wye-grounded wye connection is primarily used to supply single-phase and three-phase loads on four-wire multi-grounded systems.
  Three Phase Transformer Models
Unlike the delta-wye and wye-delta connections, there is no phase shift between the voltages and currents on the two sides of the bank.

## Slide 60
        The Grounded Wye-Grounded Wye Connection
  Three Phase Transformer Models
Figure 8.0

## Slide 61
        The Grounded Wye-Grounded Wye Connection
    With reference to Figure 8.0, the ideal transformer voltages on the secondary windings can be computed by:
    (73)
    (74)
  Three Phase Transformer Models

## Slide 62
        The Grounded Wye-Grounded Wye Connection
    The line-to-ground voltages on the primary side are related to the ideal transformer voltages by the turns ratio:
    (75)
    (76)
    Substitute equation (74) into equation (76):
    (77)
  Three Phase Transformer Models

## Slide 63
        The Grounded Wye-Grounded Wye Connection
    Equation (77) is in the generalized form with the and matrices defined by:
    (78)
    (79)
  Three Phase Transformer Models

## Slide 64
        The Grounded Wye-Grounded Wye Connection
    The primary line currents as a function of the secondary line currents is given by:
  Three Phase Transformer Models
(80)
where (81)
    The reverse equation is determined by solving equation (77) for the secondary line-to-ground voltages:
(82)

## Slide 65
  Three Phase Transformer Models
        The Grounded Wye-Grounded Wye Connection
    Constant matrices for the reverse equation are given by:
      (83)
      (84)

## Slide 66: Part 3: Three Phase Transformer Models
Three Phase Transformer Models
  General Three Phase Transformer Banks
  Generalized Matrices
  Symmetrical Components
  The Delta-Grounded Wye Step Down Connection
  The Ungrounded Wye-Delta Step Down Connection
  The Grounded Wye-Grounded Wye Connection
  The Delta-Delta Connection
  Open Wye-Open Delta
  Thevenin Equivalent Circuit

## Slide 67
        The Delta-Delta Connection
  Three Phase Transformer Models
    The delta-delta connection is primarily used on three wire systems to provide service to a three-phase load or a combination of three-phase and single-phase loads.
Figure 9.0

## Slide 68
    The basic ideal transformer voltage and current equations as a function of the turns ratio are:
    (85)
    (86)
    (87)
  Three Phase Transformer Models
        The Delta-Delta Connection

## Slide 69
    (88)
    where (89)
  Three Phase Transformer Models
        The Delta-Delta Connection
    Solve equation (88) for the source side delta currents.
(90)
    The basic ideal transformer voltage and current equations as a function of the turns ratio (continued):

## Slide 70
        The Delta-Delta Connection
    The line currents as a function of the delta currents on the source side are given by:
(91)
(92)
    Substitute equation (90) into equation (92).
(93)
  Three Phase Transformer Models

## Slide 71
        The Delta-Delta Connection
    Since is a diagonal matrix, Equation (93) can be rewritten as:
    (94)
  Three Phase Transformer Models
    The load side line currents as a function of the load side delta currents is given by:
    (95)
    (96)

## Slide 72
        The Delta-Delta Connection
    Applying equation (96), equation (94) becomes:
    (97)
    From the above equation, the load side line currents as a function of the source side line currents are given by:
    (98)
    Equation (97) and equation (98) demonstrate that the line currents on the two sides of the transformer are in phase and differ only by the turns ratio of the transformer windings.
  Three Phase Transformer Models

## Slide 73
        The Delta-Delta Connection
    The ideal delta voltages on the load side as a function of the line-to-line voltages, the delta currents, and the transformer impedances are given by:
    (99)
    where (100)
  Three Phase Transformer Models

## Slide 74
        The Delta-Delta Connection
    Substitute equation (99) into equation (86).
(101)
    Solve equation (101) for the load side line-to-line voltages.
    (102)
    The delta currents in equation (101) and equation (102) are replaced by the load side line currents .
  Three Phase Transformer Models

## Slide 75
        The Delta-Delta Connection
    Three independent equations are needed.
      Two come from applying KCL at the two vertices of the delta connected secondary.
    (103)
    (104)
      The third equation comes because the sum of the primary line-to-line voltages and, therefore, the secondary ideal transformer voltages must sum to zero. KVL around the delta windings gives:
    (105)
  Three Phase Transformer Models

## Slide 76
        The Delta-Delta Connection
    Replace the ideal delta voltages with the source side line-to-line voltages.
(106)
    As the sum of the line-to-line voltages must equal zero (KVL), and the turns ratio of the three transformers are equal, equation (106) is simplified to:
(107)
  Three Phase Transformer Models

## Slide 77
        The Delta-Delta Connection
    Equation (103), equation (104), and equation (107) can be put into the matrix form:
  (108)
    (109)
    where (110)
    (111)
  Three Phase Transformer Models

## Slide 78
        The Delta-Delta Connection
  Three Phase Transformer Models
    Solve (109) for the load side delta currents.
    (112)
    where
    (113)

## Slide 79
    Writing equation (112) in the matrix form gives:
(114)
    From equation (113) and equation (114), it can be seen that the delta currents are a function of the transformer impedances and the line currents in phases and .
  Three Phase Transformer Models
        The Delta-Delta Connection

## Slide 80
        The Delta-Delta Connection
    Equation (114) can be modified to include the line current in phase by setting the last column of the matrix to zeros.
    (115)
    The final form of equation (115) can be written as:
    (116)
    where (117)
  Three Phase Transformer Models

## Slide 81
        The Delta-Delta Connection
    The general form of the equation (117) will be used to define the generalized constant matrices for the delta-delta connection.
    Substitute equation (117) into equation (111).
    (118)
    The generalized matrices are defined in terms of the line-to-neutral voltages on the two sides of the transformer bank.
    Equation (118) is modified to be in terms of equivalent line-to-neutral voltages
(119)
  Three Phase Transformer Models

## Slide 82
        The Delta-Delta Connection
    Equation (119) is in the general form:
    (120)
    where (121)
    (122)
  Three Phase Transformer Models

## Slide 83
    Equation (97) gives the generalized equation for currents.
    (123)
where (124)
  Three Phase Transformer Models
        The Delta-Delta Connection

## Slide 84
    The reverse generalized equation can be derived by modifying Equation (102) in terms of equivalent line-to-neutral voltages.
(125)
      (126)
where (127)
(128)
  Three Phase Transformer Models
        The Delta-Delta Connection

## Slide 85: Part 3: Three Phase Transformer Models
Three Phase Transformer Models
  General Three Phase Transformer Banks
  Generalized Matrices
  Symmetrical Components
  The Delta-Grounded Wye Step Down Connection
  The Ungrounded Wye-Delta Step Down Connection
  The Grounded Wye-Grounded Wye Connection
  The Delta-Delta Connection
  Open Wye-Open Delta
  Thevenin Equivalent Circuit

## Slide 86
        Open Wye-Open Delta
    A distribution feeder commonly serves a combination of both single phase and three phase loads.
    This combination can be served with an ungrounded wye-delta connection as previously described.
    When the three phase load is small compared to the single phase load, the “open wye-open delta” combination is commonly used.
    The advantage of the open wye-open delta connection is that it requires only two transformers, but can provide three-phase line-to-line voltages to the combination load.
  Three Phase Transformer Models

## Slide 87
  Three Phase Transformer Models
        Open Wye-Open Delta
Figure 10.0
    Figure 10.0 shows the open wye-open delta connection and the primary and secondary positive sequence voltage phasors.

## Slide 88
        Open Wye-Open Delta
    With reference to Figure 10.0, the basic ideal transformer voltages as a function of the “turns ratio” are:
    (129)
    (130)
  Three Phase Transformer Models

## Slide 89
        Open Wye-Open Delta
    The currents as a function of the turns ratio are given by:
  Three Phase Transformer Models
(131)
    Equation (131) can be expressed in matrix form by:
    (132)
    (133)

## Slide 90
  Three Phase Transformer Models
        Open Wye-Open Delta
    The ideal voltages on the delta windings can be determined by:
    Apply equation (129) to equation (134).
(134)
(135)

## Slide 91
        Open Wye-Open Delta
    Equation (135) can be put into three-phase matrix form as:
    (136)
    (137)
    The secondary line-to-line voltages in equation (137) can be replaced by the equivalent line-to-neutral secondary voltages.
    (138)
  Three Phase Transformer Models

## Slide 92
        Open Wye-Open Delta
    The generalized matrix equation becomes:
    (139)
    where (140)
    (142)
  Three Phase Transformer Models

## Slide 93
  Three Phase Transformer Models
        Open Wye-Open Delta
    The source side line currents as a function of the load side line currents are given by:
(143)
(144)
where (145)

## Slide 94
  Three Phase Transformer Models
        Open Wye-Open Delta
    For deriving the reverse equation, relating the secondary equivalent line-to-neutral voltages as a function of the source side line-to-ground voltages and line currents, we first obtain the two line-to-line secondary voltages.
(146)

## Slide 95
        Open Wye-Open Delta
    The third line-to-line voltage () must be equal to the negative sum of the other two line-to-line voltages(KVL). In the matrix form, the desired equation is:
    (147)
    (148)
  Three Phase Transformer Models

## Slide 96
    The generalized reverse equation is given by:
    (150)
  Three Phase Transformer Models
        Open Wye-Open Delta
    The equivalent secondary line-to-neutral voltages are given by:
and
(149)

## Slide 97
    where
    (151)
    (152)
  Three Phase Transformer Models
        Open Wye-Open Delta

## Slide 98
        Open Wye-Open Delta
    The equations derived on the previous slide are for an open-wye-open delta connection on phases A and B on the primary.
    The same methodology can be adopted to derive the equations when the transformers are on phases B and C or A and C on the primary.
    The terms “leading” and “lagging” connection are also associated with the open wye-open delta connection.
  Three Phase Transformer Models

## Slide 99
        Open Wye-Open Delta
    When the “lighting” transformer is connected across the leading of the two phases, it is known as “leading” connection.
      For example when connected from phase A to ground, the connection would be known as a leading connection.
    When the “lighting” transformer is connected across the lagging of the two phases, it is known as a “lagging” connection.
      For example, when the connection is from the ground to phase A, it is known as a lagging connection
  Three Phase Transformer Models

## Slide 100: Part 3: Three Phase Transformer Models
Three Phase Transformer Models
  General Three Phase Transformer Banks
  Generalized Matrices
  Symmetrical Components
  The Delta-Grounded Wye Step Down Connection
  The Ungrounded Wye-Delta Step Down Connection
  The Grounded Wye-Grounded Wye Connection
  The Delta-Delta Connection
  Open Wye-Open Delta
  Thevenin Equivalent Circuit

## Slide 101
        Thevenin Equivalent Circuit
    The Thevenin equivalent circuit referenced to the secondary terminals of the transformer must take into account the equivalent impedance between the primary terminals of the transformer and the feeder source.
    Figure 11.0 is a general circuit showing the feeder source down to the secondary bus.
      Figure 11.0
  Three Phase Transformer Models

## Slide 102
        Thevenin Equivalent Circuit
    The Thevenin equivalent is obtained by “referring” the source voltage and the source impedance to the secondary side of the transformer.
  Three Phase Transformer Models
    The desired Thevenin equivalent circuit at the transformer secondary node is shown in Figure 12.0.
    Figure 12.0

## Slide 103
        Thevenin Equivalent Circuit
    In Figure 11.0, the primary transformer equivalent line-to-neutral voltages as a function of the source voltage and the equivalent high side impedance is given by:
    (153)
    But
    Therefore,
    (154)
  Three Phase Transformer Models

## Slide 104
        Thevenin Equivalent Circuit
    The general reverse equation gives the secondary line-to-neutral voltages as a function of the primary line-to-neutral voltages:
    (155)
    Substitute equation (154) into equation (155).
(156)
  Three Phase Transformer Models

## Slide 105
        Thevenin Equivalent Circuit
    With reference to equation (156), the Thevenin equivalent voltages and impedances can be defined as:
(157)
    (158)
    The definition of the Thevenin equivalent voltages and impedances as given in equation (157) and equation (158) are general and can be used for all transformer connections.
  Three Phase Transformer Models

## Slide 106: Part 4: Center –Tapped Transformers and Secondaries
Center –Tapped Transformers and Secondaries
  Center-Tapped Single-Phase Transformer
    Matrix Equations
    Center-Tapped Transformer Serving Loads through a Triplex Secondary
  Underground Wye-Delta Transformer Bank with a Center Tapped Transformer
  Leading Open Wye-Open Delta Transformer Connection
  Lagging Open Wye-Open Delta Connection
  Four Wire Secondary

## Slide 107
    The standard method of providing three-wire service is from a center-tapped single-phase transformer.
    In this type of connection there are two 120 volt circuits and one 240-volt circuit.
    There are two types of center tapped transformers.
Center-Tapped Single-Phase Transformer

## Slide 108
    The first is as shown in Figure 13.0.
    Figure 13.0
    Here the secondary consists of one winding that is center tapped. The secondary voltage of this transformer will be specified as 240/120 volts.
    The 240/120 volts secondary rating specifies that the full winding voltage is 240 volts with the center tap providing two 120 volt circuits.
Center-Tapped Single-Phase Transformer

## Slide 109
    A second type is as shown in Figure 14.0.
        Figure 14.0
    Here the transformer consists of a three winding transformer with the two secondary windings connected in series.
    The secondary of this transformer is specified in 120/240 volts.
Center-Tapped Single-Phase Transformer

## Slide 110
    The model of the center-tapped transformer of Figure 13.0 and 14.0 is shown in Figure 15.0.
    Figure 15.0
    It can either represent the model of the center tapped transformer of Figure 13.0 or the two secondary windings connected in series of Figure 14.0.
Center-Tapped Single-Phase Transformer

## Slide 111
    The first step to developing the model is to determine the impedances , , .
    The values of and in per-unit based upon transformer ratings are given in Turan Gonen’s Electric Power Distribution System Engineering.
    Empirical equations are commonly used to convert the transformer impedance to the winding impendences.
Center-Tapped Single-Phase Transformer

## Slide 112
    For an interlaced designed, these equations are given by:
(159)
    For a non-interlaced designed, these equations are given by:
    (160)
Center-Tapped Single-Phase Transformer

## Slide 113: Part 4: Center –Tapped Transformers and Secondaries
Center –Tapped Transformers and Secondaries
  Center-Tapped Single-Phase Transformer
    Matrix Equations
    Center-Tapped Transformer Serving Loads through a Triplex Secondary
  Underground Wye-Delta Transformer Bank with a Center Tapped Transformer
  Leading Open Wye-Open Delta Transformer Connection
  Lagging Open Wye-Open Delta Connection
  Four Wire Secondary

## Slide 114
        Matrix Equations
      Referring to Figure 13.0, the ideal secondary voltages of the transformer are:
Center-Tapped Single-Phase Transformer
(161)
(162)

## Slide 115
        Matrix Equations
      The ideal primary voltage as a function of the secondary ideal voltages is:
        where (163)
Center-Tapped Single-Phase Transformer
(162)

## Slide 116
Center-Tapped Single-Phase Transformer
        Matrix Equations
      The primary transformer current as a function of the secondary winding currents is given in equation (164).
      The negative sign is due to the selected direction of the current
(164)

## Slide 117
Center-Tapped Single-Phase Transformer
        Matrix Equations
      Substitute equations (161) into equations (162).
(165)
      The source voltage as a function of the ideal primary voltage is:
(166)

## Slide 118
        Matrix Equations
      Substitute equations (165) into equations (166):
          (167)
      Substitute equations (164) into equations (167):
Center-Tapped Single-Phase Transformer
(168)

## Slide 119
        Matrix Equations
      Equation (168) is of the form:
(169)
      where
    (170)
Center-Tapped Single-Phase Transformer
(171)

## Slide 120
        Matrix Equations
    Equation (164) is of the form:
where (172)
    Equation (169) is used to compute the primary source voltage when the secondary terminal voltages and the secondary currents are known.
Center-Tapped Single-Phase Transformer

## Slide 121
Center-Tapped Single-Phase Transformer
        Matrix Equations
    The reverse equations for determining the secondary terminal voltage when the primary source voltage and secondary currents are known are obtained by solving equation (169) for the secondary terminal voltages.
    (173)

## Slide 122
Center-Tapped Single-Phase Transformer
        Matrix Equations
where
    (174)

## Slide 123: Part 4: Center –Tapped Transformers and Secondaries
Center –Tapped Transformers and Secondaries
  Center-Tapped Single-Phase Transformer
    Matrix Equations
    Center-Tapped Transformer Serving Loads through a Triplex Secondary
  Underground Wye-Delta Transformer Bank with a Center Tapped Transformer
  Leading Open Wye-Open Delta Transformer Connection
  Lagging Open Wye-Open Delta Connection
  Four Wire Secondary

## Slide 124
  Center-Tapped Transformer Serving Loads through a Triplex Secondary
    Figure 16.0 shows a center-tapped transformer serving a load through a triplex secondary.
        Figure 16.0
Center-Tapped Single-Phase Transformer

## Slide 125
    The impedance matrix of the triplex secondary is determined using Carson’s equation.
    Apply Carson’s equations:
Center-Tapped Single-Phase Transformer
  Center-Tapped Transformer Serving Loads through a Triplex Secondary
    A triplex secondary consisting of two insulated conductors and one un-insulated neutral conductor is as shown in Figure 17.0.
Figure 17.0
(175)

## Slide 126
  Center-Tapped Transformer Serving Loads through a Triplex Secondary
    The secondary voltage equation in the matrix form is:
(176)
    When the neutral is grounded at the transformer and the load then:
(177)
    This leads to the Kron reduction equation in partitioned form:
      (178)
Center-Tapped Single-Phase Transformer

## Slide 127
    Solving equation (178) for the neutral current:
  define (180)
Center-Tapped Single-Phase Transformer
  Center-Tapped Transformer Serving Loads through a Triplex Secondary
(179)

## Slide 128
  Center-Tapped Transformer Serving Loads through a Triplex Secondary
    Substituting equation (178) into equation (180) and solving for the voltage drops we get:
(181)
define
(182)
Center-Tapped Single-Phase Transformer

## Slide 129
  Center-Tapped Transformer Serving Loads through a Triplex Secondary
    For a secondary of length :
  (183)
    Referring to Figure 16.0, the secondary output voltages of the transformer are given by:
    (184)
    The transformer primary voltage is given by equation (172).
Center-Tapped Single-Phase Transformer

## Slide 130
  Center-Tapped Transformer Serving Loads through a Triplex Secondary
    Substituting equation (184) into equation (172):
(185)
where
Center-Tapped Single-Phase Transformer

## Slide 131
Center-Tapped Single-Phase Transformer
  Center-Tapped Transformer Serving Loads through a Triplex Secondary
    Since there are no shunt elements in the secondary, the primary current as a function of the secondary currents is still given by equation (164).
    Equation (185) can be used to solve for the load voltages when the primary source voltages and the secondary currents are known.
    where (186)

## Slide 132
Center-Tapped Single-Phase Transformer
  Center-Tapped Transformer Serving Loads through a Triplex Secondary
    In the matrix form, equation (186) can be given by:
(187)

## Slide 133: Part 4: Center –Tapped Transformers and Secondaries
Center –Tapped Transformers and Secondaries
  Center-Tapped Single-Phase Transformer
    Matrix Equations
    Center-Tapped Transformer Serving Loads through a Triplex Secondary
  Underground Wye-Delta Transformer Bank with a Center Tapped Transformer
  Leading Open Wye-Open Delta Transformer Connection
  Lagging Open Wye-Open Delta Connection
  Four Wire Secondary

## Slide 134
  Underground Wye-Delta Transformer Bank with a Center Tapped Transformer
    Ungrounded wye-delta transformer connection is used for providing service to a combination of three-phase and single-phase loads.
    In order to provide three-wire service for single-phase loads, one of the transformers is a center tap transformer.
    This transformer is called the “lighting” transformer and the other two transformers are called the “power” transformers.
Center-Tapped Single-Phase Transformer

## Slide 135
Center-Tapped Single-Phase Transformer
  Underground Wye-Delta Transformer Bank with a Center Tapped Transformer
    Figure 18.0 : Ungrounded wye-delta with center-tapped transformer

## Slide 136
  Underground Wye-Delta Transformer Bank with a Center Tapped Transformer
      Backward Sweep Equations
    In order to compute the source side voltages and currents from the secondary side voltages and currents, from Figure 18.0, define the secondary terminal voltages as:
(188)
Center-Tapped Single-Phase Transformer

## Slide 137
  Underground Wye-Delta Transformer Bank with a Center Tapped Transformer
    The secondary line currents and the currents flowing inside the delta are defined as:
      (189) (190)
    The transformer ratio is defined as:
(191)
Center-Tapped Single-Phase Transformer

## Slide 138
  Underground Wye-Delta Transformer Bank with a Center Tapped Transformer
    The matrix equation relating the primary ideal transformer voltages to the secondary ideal voltages is:
    (192)
    The primary terminal voltages are given by:
(193)
Center-Tapped Single-Phase Transformer

## Slide 139
  Underground Wye-Delta Transformer Bank with a Center Tapped Transformer
    Substitute equation (192) into equation (193).
(194)
    The primary line currents as a function of the secondary delta currents are given by:
(195)
Center-Tapped Single-Phase Transformer

## Slide 140
  Underground Wye-Delta Transformer Bank with a Center Tapped Transformer
    Substitute equation (195) into equation (194):
(196)
    The secondary ideal transformer voltages are given by:
(197)
Center-Tapped Single-Phase Transformer

## Slide 141
    Substitute equation (190) into equation (196):
(198)
Center-Tapped Single-Phase Transformer
  Underground Wye-Delta Transformer Bank with a Center Tapped Transformer

## Slide 142: Part 4: Center –Tapped Transformers and Secondaries
Center –Tapped Transformers and Secondaries
  Center-Tapped Single-Phase Transformer
    Matrix Equations
    Center-Tapped Transformer Serving Loads through a Triplex Secondary
  Underground Wye-Delta Transformer Bank with a Center Tapped Transformer
  Leading Open Wye-Open Delta Transformer Connection
  Lagging Open Wye-Open Delta Connection
  Four Wire Secondary

## Slide 143
  Leading Open Wye-Open Delta Transformer Connection
The leading open wye-open delta connection consists of one lighting and one power transformer used to serve a combination of single-phase and three-phase loads.
The leading open wye-open delta connection and the no-load voltage phasors for this connection are as shown in Figure 19.0 and Figure 20.0.
Center-Tapped Single-Phase Transformer

## Slide 144
  Leading Open Wye-Open Delta Transformer Connection
Center-Tapped Single-Phase Transformer
Figure 19.0

## Slide 145
Unlike the closed delta, there is a direct relationship between the secondary transformer currents and the line currents.
Hence, applying KCL in Figure 19.0, the currents flowing in the open delta as a function of the line currents are given by:
Center-Tapped Single-Phase Transformer
  Leading Open Wye-Open Delta Transformer Connection
Figure 20.0
(200)

## Slide 146
The primary and secondary ideal transformer voltages going from the secondary to the primary are related by:
(201)
Center-Tapped Single-Phase Transformer
  Leading Open Wye-Open Delta Transformer Connection

## Slide 147
Center-Tapped Single-Phase Transformer
  Leading Open Wye-Open Delta Transformer Connection
The primary and transformer secondary currents are related by:
(202)

## Slide 148
  Leading Open Wye-Open Delta Transformer Connection
Going from the primary ideal transformer voltages to the secondary ideal voltages (forward sweep), the voltages are related by:
(203)
Center-Tapped Single-Phase Transformer

## Slide 149
For this open wye-open delta connection, the transformer impedance matrices are defined as:
(204)
Center-Tapped Single-Phase Transformer
  Leading Open Wye-Open Delta Transformer Connection

## Slide 150
Equation (199):
Center-Tapped Single-Phase Transformer
  Leading Open Wye-Open Delta Transformer Connection
(199)
Equation (199) is now used to determine the forward and backward matrices.

## Slide 151: Part 4: Center –Tapped Transformers and Secondaries
Center –Tapped Transformers and Secondaries
  Center-Tapped Single-Phase Transformer
    Matrix Equations
    Center-Tapped Transformer Serving Loads through a Triplex Secondary
  Underground Wye-Delta Transformer Bank with a Center Tapped Transformer
  Leading Open Wye-Open Delta Transformer Connection
  Lagging Open Wye-Open Delta Connection
  Four Wire Secondary

## Slide 152
  Lagging Open Wye-Open Delta Connection
In the lagging open wye-open delta connection, the transformer serving the single phase load is connected across the voltage that lags the power transformer by 120 degrees.
Center-Tapped Single-Phase Transformer
A number of connections can be used to achieve the lagging open wye-open delta connection, Figure 21.0 shows the connection that will be used here.

## Slide 153
  Lagging Open Wye-Open Delta Connection
Center-Tapped Single-Phase Transformer
Figure 21.0

## Slide 154
In Figure 21.0, the lighting transformer is connected to phase C and the power transformer is connected to phase A.
The no-load phasor voltage phasor diagrams for this connection are shown in Figure 22.0.
                Figure 22.0
Center-Tapped Single-Phase Transformer
  Lagging Open Wye-Open Delta Connection

## Slide 155
  Lagging Open Wye-Open Delta Connection
With this connection, the phasing of the secondary will remain the same as the leading connection. Hence the definition of the matrix will remain the same as equation (200).
The primary and the secondary ideal transformer voltages going from the secondary to the primary are related by:
(205)
Center-Tapped Single-Phase Transformer

## Slide 156
  Lagging Open Wye-Open Delta Connection
The primary and transformer secondary currents are related by:
(206)
Center-Tapped Single-Phase Transformer

## Slide 157
Going from the primary ideal transformer voltages to the secondary ideal voltages (forward sweep) the voltages are related by:
(207)
Center-Tapped Single-Phase Transformer
  Lagging Open Wye-Open Delta Connection

## Slide 158
For this open wye-open delta connection, the transformer impedance matrix are defined as:
(208)
    Equation (199) is again used to determine the forward and backward matrices.
Center-Tapped Single-Phase Transformer
  Lagging Open Wye-Open Delta Connection

## Slide 159: Part 4: Center –Tapped Transformers and Secondaries
Center –Tapped Transformers and Secondaries
  Center-Tapped Single-Phase Transformer
    Matrix Equations
    Center-Tapped Transformer Serving Loads through a Triplex Secondary
  Underground Wye-Delta Transformer Bank with a Center Tapped Transformer
  Leading Open Wye-Open Delta Transformer Connection
  Lagging Open Wye-Open Delta Connection
  Four Wire Secondary

## Slide 160
  Four Wire Secondary
Typically a combination of single-phase and three-phase loads will be connected to transformer through a length of open four-wire secondary or a quadraplex cable secondary.
Center-Tapped Single-Phase Transformer
Figure 23.0

## Slide 161
The self and mutual impedances of the four-wire secondary are calculated using Carson’s equations and Kron reduction, thus giving a 3X3 impedance matrix.
The voltage drops on the three line conductors are:
(209)
Center-Tapped Single-Phase Transformer
  Four Wire Secondary

## Slide 162
      Write the KVL around the three “window” loops and the outside loop in Figure 21.0.
(210)
Center-Tapped Single-Phase Transformer
  Four Wire Secondary

## Slide 163
Substitute Equation (109) into Equation (210).
(211)
Center-Tapped Single-Phase Transformer
  Four Wire Secondary

## Slide 164
Center-Tapped Single-Phase Transformer
  Four Wire Secondary
Equation (211) is in the form of:
where
(212)

## Slide 165
  Four Wire Secondary
Since there are no shunt devices between the transformer and the loads, the currents leaving the transformer are equal to the line currents serving the loads. Thus
(213)
  The matrices for the forward sweep are:
(214)
Center-Tapped Single-Phase Transformer

## Slide 166: Part 4: IEEE Test Systems
  IEEE 4 Bus System
  IEEE 13 Bus System
  IEEE 37 Bus System
  IEEE 8500 Node System

## Slide 167
  IEEE Test Systems
  IEEE 4 Bus System

## Slide 168
  IEEE Test Systems
  IEEE 13 Bus System

## Slide 169
  IEEE Test Systems
  IEEE 37 Bus System

## Slide 170
  IEEE Test Systems
  IEEE 8500 Node System