## Slide 1: Substation and Distribution Automation
Module 3: Distribution level power flow

## Slide 2: Module 3 Overview
Part 1 - Review of Balanced Powerflow Techniques
Part 2 - Forward Backward Sweep (FBS) Method
Part 3 - Three Phase Current Injection (TCIM) Newton Raphson (NR) Method

## Slide 3: Part 1 - Review of Balanced Power Flow
Powerflow is the fundamental analysis tool and provides the input information for many planning and operations tools.
Powerflow was originally developed only for the transmission level because of the cost of computing.
To further reduce computing requirements a number of assumptions were made:
  Balanced system
  Transposed transmission lines
  Loads are constant power

## Slide 4: The Powerflow Problem
The goal of powerflow is to determine the voltage and angle at all nodes in the system, when given the end-use load and generator inputs.
To relate the two sets of variables the powerflow problem breaks the system into two concepts:
  Power injections
  Network formulation

## Slide 5: The Powerflow Problem Cont.
Power Injections
Network Formulation

## Slide 6: Power Injections
Injection of power at a node is from the perspective of the interconnecting transmission system.
  A positive injection indicates generated power.
  A negative injection indicates consumed power.
The node injections are generally known for all but one bus in advance. This is known as the swing or slack bus.
The net complex power injected into a bus is given by
where complex power supplied by the generator is:
and the complex power consumed by the loads is:
(1)
(2)
(3)

## Slide 7: The Network Formulation
In addition to the power injections that occur due to the generators and the loads, power flows into and out of each node on the interconnecting lines.
These flows are not injections from the perspective of the transmission system, they are simple flows between nodes.
Given the voltage and angle at the nodes on either end of a line, the flows can be determined.
Because of the potentially large number of nodes and links, these equations are formulated with sets of equations.

## Slide 8: The Network Formulation Cont.
The network consists of the lines and transformers that connect the nodes of a system.
While the diagram shows only a single line, three phases are actually represented.
The power that is injected at the nodes flows across the lines.

## Slide 9: The Network Formulation Cont.
The “pi” model is a common representation for a transmission line.
There are two parts:
  A series impendence
  Two shunt capacitances
The pi model is adequate for a single line section when solving for a steady state values, i.e. powerflow.

## Slide 10: The Network Formulation Cont.
A node will often have multiple lines connected to it.
The capacitance values from the multiple lines can be combined into a single effective value.
The resultant model is a series impendence between each node, and a single shunt value.

## Slide 11
The lumped shunt capacitance values can determined using the equations of (4).
(4)
  The Network Formulation Cont.

## Slide 12
Besides the ground node, there are four other nodes (buses) at which the current from the sources is injected into the network.
Applying Kirchhoff’s current law (KCL) at nodes 1,2,3 and 4, respectively, to get the following four equations:
(5)
  The Network Formulation Cont.

## Slide 13: The Network Formulation Cont.
(6)
Rearranging and writing in matrix form gives:
Equation (6) is for a system with 4 nodes, but the general formulation can be expanded to include any number of nodes.
When the correct values of voltage are known, the currents calculated in equation (6) will equal the currents of the node injections from generation and load.

## Slide 14
Equation (7) can be recognized to be of the standard form:
(7)
(8)

## Slide 15
Each off-diagonal term Yik (I, k = 1,2,3,4) is the mutual admittance (transfer admittance) between nodes i and k and equals the negative of the sum of all admittances connected directly between these nodes.
Further, Yik = Yki
Each admittance Yii (i = 1,2,3,4) is called the self admittance (or driving point admittance) of node i and equals the algebraic sum of all the admittances terminating on the node.
  The Network Formulation Cont.

## Slide 16
(8)
From index notation, Eq. (8) can be written in compact form as:
(9)
or, in matrix form:
(10)
where YBUS denotes the matrix of bus admittance and is
known as bus admittance matrix.
The dimension of the YBUS matrix is (n × n) where n is the number of buses.
The total number of nodes are m = n + 1 including the ground (reference) node.
  The Network Formulation Cont.

## Slide 17
The complex power injected by the source into the ith bus of a power system is:
where Vi is the voltage at the th bus with respect to ground and Ii is the source current injected into the bus.
(11)
The load flow problem is handled more conveniently by use of Ii rather than Ii*.
  Powerflow Formulation
As shown in (11), the power injections should equal the network flows.

## Slide 18
Therefore, taking the complex conjugate of Eq. (11) gives:
(12)
Substitute from Eq. (9) to get:
(13)
  Powerflow Formulation Cont.

## Slide 19
Equating real and imaginary parts:
In polar form:
(14)
(15)
(16)
  Powerflow Formulation Cont.

## Slide 20
Real and reactive power flows between lines can be calculated:
(17)
(18)
  Powerflow Formulation Cont.
Because there are no energy storage elements, the complex power flows in (17) and (18) are equal to the power injections in (1)-(3).
By relating these equations, the fundamental power flow equations are derived.

## Slide 21
Equations (19) and (20) represent 2n power flow equations at n buses of a power system (n real power flow equations and n reactive power flow equations).
Each bus is characterized by four variables; , , and , resulting in a total of 4n variables.
Equations (19) and (20) can be solved for 2n variables if the remaining 2n variables are specified.
  Powerflow Formulation Cont.
(19)
(20)

## Slide 22
Practical considerations allow a power system analyst to fix a priori two variables at each bus.
The solution for the remaining 2n bus variables is obtained by iterative numerical techniques.
Depending upon which two variables are specified, the buses are classified into three categories – PQ Buses (Load Buses), PV Buses (Generator Buses), Slack or Reference Bus.
Slack bus (ref. bus) - Voltage magnitude and angle known : ,
PV Bus : real power and voltage magnitude known : ,
PQ Bus : real and reactive powers known : ,
  Powerflow Considerations

## Slide 23
When we solve the power flow problem, all the variables must lie within practical limits.
Voltage magnitude must satisfy the inequality:
(19)
(ii) Certain of the ’s must satisfy the inequality constraint:
(20)
(iii) Physical limitations on the generators, PGi and QGi are constrained as follows:
(21)
(22)
  Powerflow Considerations

## Slide 24
The total generation of real and reactive power must equal the total load demand plus losses, i.e.,
where PL and QL are system real and reactive power loss, respectively
  Powerflow Considerations
(23)
(24)

## Slide 25: Power Flow Solution Techniques
Once the non-linear power flow problem is properly formulated it is necessary to solve the equations.
Since the problem is highly non-linear and an analytic solution is not readily available, iterative solver are commonly used.
The following sections will examine some of the most common solution techniques.

## Slide 26: Power Flow Solution Techniques
Review of balanced power flow
  Gauss Iterative Technique
  Gauss-Seidel Iterative Technique
  Newton Raphson
  Fast Decoupled
  DC Power Flow

## Slide 27: Gauss Iterative Technique
Given ,,…… , we need to find ,,…… .
Knowing , ……, it is possible to find . Since is already known, only , ……, need to be found. These unknowns may be found from the equations of (26).
Taking the complex conjugate, replace (25) and (26) by:
(27)
(25)
(26)

## Slide 28: Gauss Iterative Technique
Dividing (27) by and separating out the term, (27) can be rewritten as:
  or, rearranging:
(28)
(29)

## Slide 29: Gauss Iterative Technique
Thus, we get implicit nonlinear algebraic equations in the unknown complex in the form:
where the are given by (29).
The numbering of (30) can be changed such that =, =.
(30)

## Slide 30: Gauss Iterative Technique
In vector notation, (30) is written in the form :
(31)
Solving (31) by iteration we get
(32)
  where the superscript indicates the iteration number.
Thus, starting with an initial value , a sequence of , , ……are generated until convergence is achieved.

## Slide 31: Gauss Iterative Technique
In practice, the iterations are stopped when the changes in become very small.
T is the Euclidean norm
Thus, Gauss iteration, v = 0,1,2,…..:
(33)

## Slide 32: Power Flow Solution Techniques
Review of balanced power flow
  Gauss Iterative Technique
  Gauss-Seidel Iterative Technique
  Newton Raphson
  Fast Decoupled
  DC Power Flow

## Slide 33: Gauss-Seidel Iterative Technique
Recall: Gauss iteration, v = 0,1,2,…..:
When is being solved, would be known. Since is a better estimate than , the updated value is used.
Similarly, when solving for , then and can be used. This modification is called the Gauss-Seidel iteration.
(33)

## Slide 34: Gauss-Seidel Iterative Technique
Gauss-Seidel iteration, v = 0,1,2,…..:
(34)

## Slide 35: Power Flow Solution Techniques
Review of balanced power flow
  Gauss Iterative Technique
  Gauss-Seidel Iterative Technique
  Newton Raphson
  Fast Decoupled
  DC Power Flow

## Slide 36: Newton Raphson Method
Newton-Raphson Methods were originally developed for use on transmission level analysis.
They are based on the power injections at each node, both real and reactive.
These power injections are then used to update the voltage and voltage angle.
The NR method is a powerful method of solving a system of non-linear algebraic equations, requiring the calculation and inversion of a Jacobian matrix, which is computationally intensive.
It solves in a relatively few number of iterations.
It is the most widely used method for solving power flow problem.

## Slide 37
Consider a set of non-linear algebraic equations:
(35)
Assume initial values of unknowns as , ,…, .
Let , ,…, be the corrections, which upon being added to the initial guess, give the actual solution.
Therefore:
(36)
Newton Raphson General Form

## Slide 38
Expanding these equations in Taylor series around the initial guess gives:
where , are the derivatives of fi with respect to x1, x2, …., xn evaluated at .
Newton Raphson General Form
(37)

## Slide 39
Neglecting higher order terms, write the above equation in matrix form.
Newton Raphson General Form
(38)

## Slide 40
Equation (38) can also be expressed as:
(39)
is known as the Jacobian matrix (obtained by differentiating the function vector f with respect to x and evaluating it at x0)
Equation (39) can be rearranged:
(40)
Newton Raphson General Form

## Slide 41
Approximate values of corrections can be obtained from Eq. (40). These being a set of linear algebraic equations that can be solved efficiently by triangularization and back substitution.
For the th iteration:
Iterations are continued until Eq. (35) is satisfied to any desired accuracy, i.e.,
Newton Raphson General Form
(41)
(42)

## Slide 42: Newton Raphson For Power Systems
(43)

## Slide 43: Newton Raphson For Power Systems
Consider Eq’s 43 re-written:
such that and are functions of , with
being the vector of ’s, and the vector of ’s.
The vector f(x) may be expressed as:
where is the vector of ’s, and the vector of ’s.
(44)

## Slide 44: Newton Raphson For Power Systems
From equation (40):
(45)
Equation (45) shows how the state variable can be solved for each iteration.
The number of iterations depends on the desired accuracy.

## Slide 45: Worked Powerflow Examples
Gauss Siedel
Newton Raphson

## Slide 46: Gauss-Seidel Worked Example
Example A: Gauss-Seidel Power Flow
Figure 5 shows a single-line diagram of a five-bus power system. The four tables on the following slides contain input data.

## Slide 47
Bus | Type | V per unit | degrees | per unit | per unit | per unit | per unit | per unit | per unit
1 | Swing | 1.0 | 0 | - | - | 0 | 0 | - | -
2 | Load | - | - | 0 | 0 | 8 | 2.8 | - | -
3 | Constant Voltage | 1.05 | - | 5.2 | - | .8 | .4 | 4 | -2.8
4 | Load | - | - | 0 | 0 | 0 | 0 | - | -
5 | Load | - | - | 0 | 0 | 0 | 0 | - | -
Bus | Type | V per unit |  |  |  |  |  |  | 
1 | Swing | 1.0 | 0 | - | - | 0 | 0 | - | -
2 | Load | - | - | 0 | 0 | 8 | 2.8 | - | -
3 | Constant Voltage | 1.05 | - | 5.2 | - | .8 | .4 | 4 | -2.8
4 | Load | - | - | 0 | 0 | 0 | 0 | - | -
5 | Load | - | - | 0 | 0 | 0 | 0 | - | -
Table 1: Bus input Data for Example A
Bus 1 has a generator connected and is a swing bus.
Bus 3 has a generator and a load connected. It is a voltage controlled bus.
Buses 2,3, and 5 are all load buses.

## Slide 48
Bus-to-Bus | R’ per unit | X’ per unit | G’ per unit | B’ per unit | Maximum MVA per unit
2-4 | 0.0090 | 0.100 | 0 | 1.72 | 12.0
2-5 | 0.0045 | 0.050 | 0 | 0.88 | 12.0
4-5 | 0.00225 | 0.025 | 0 | 0.44 | 12.0
Bus-to-Bus | R per unit | X per unit | per unit | per unit | Maximum MVA per unit | Maximum TAP Setting per unit
1-5 | 0.00150 | 0.02 | 0 | 0 | 6.0 | -
3-4 | 0.00075 | 0.01 | 0 | 0 | 10.0 | -
Bus-to-Bus | R per unit | X per unit |  |  | Maximum MVA per unit | Maximum TAP Setting per unit
1-5 | 0.00150 | 0.02 | 0 | 0 | 6.0 | -
3-4 | 0.00075 | 0.01 | 0 | 0 | 10.0 | -
Table 2: Line input Data for Example A
Table 3: Transformer input Data for Example A

## Slide 49
Bus | Input Data | Unknowns
1 |  | 
2 |  | 
3 |  | 
4 |  | 
5 |  | 
Bus | Input Data | Unknowns
1 |  | 
2 |  | 
3 |  | 
4 |  | 
5 |  | 
Table 4: Input Data and Unknowns for Example A
Now compute the elements of the second row of
Since buses 1 and 3 are not directly connected to bus 2,

## Slide 50: Gauss-Seidel Worked Example
By using values from Table 2, compute the following.
per unit
per unit
per unit

## Slide 51: Gauss-Seidel Worked Example Cont.
Note that half the shunt admittance of each line connected to bus 2 is included in , and the other half is at the other end of these lines.
Nodal equations for the power system network may now be written as
.
For each load bus, is calculated by
  .
Applying the Gauss-Seidel power flow method to the nodal equations, with as expressed above, gives
The above equation can be applied twice during each iteration, first using , then replacing that by on the right side.

## Slide 52: Gauss-Seidel Worked Example
For a voltage-controlled bus, is unknown, but can be calculated from the following.
Now, use Gauss-Seidel to calculate the phasor voltage at load bus 2 after the first iteration ().
per unit

## Slide 53: Gauss-Seidel Worked Example
Now recalculate using = in place of .
per unit
After performing computations at buses 3, 4, and 5, the first Guess-Seidel iteration will be complete.

## Slide 54: Newton Raphson Worked Example
This is a transmission level system.
  3 nodes
  2 generators
  1 load
The transmission lines are assumed to be purely inductive, with no resistance.
Node types:
  Node1 :Swing bus
  Node 2: PV bus
  Node 3: PQ bus

## Slide 55: Newton Raphson Worked Example
(46)
(47)
(48)

## Slide 56: Newton Raphson Worked Example
(49)
(50)

## Slide 57: Newton Raphson Worked Example

## Slide 58: Part 1 - Review of balanced power flow
Review of balanced power flow
  Gauss Iterative Technique
  Gauss-Seidel Iterative Technique
  Newton Raphson
  Fast Decoupled
  DC Power Flow

## Slide 59: Fast Decoupled Power Flow
As described in the Newton Raphson section, the Jacobian Matrix can be expressed as
The values of the off-diagonal sub-matrices and are small and can be approximated to zero.
Hence, the power flow problem can be decoupled.
(51)

## Slide 60: Fast Decoupled Power Flow
Substitute approximations into Eq. (48).
Then,
(52)

## Slide 61: Fast Decoupled Power Flow
Further assumptions can be made about the terms in and .
Usually the terms of the are smaller than the and can be ignored.
All per unit bus voltage magnitudes are considered approximately equal and difference between bus angles are considered small.

## Slide 62: Fast Decoupled Power Flow
Then, the diagonal terms of and can be written as:
(53)
(54)

## Slide 63: Fast Decoupled Power Flow
The off-diagonal terms of and can be written as:
(55)

## Slide 64
Consider and ,
where B may obtained from by stripping away the first row and column and then taking the imaginary part.
Then,
Fast Decoupled Power Flow
(56)

## Slide 65
Substitute into Eq. 52 to get:
Because of the assumption that all per unit are equal, assume the second in (57) is the identity matrix.
Thus
Note that and are just scaled versions of and .
Fast Decoupled Power Flow
(57)
(58)

## Slide 66: Fast Decoupled Power Flow
An important observation is that B is a constant matrix, independent of iteration count. Thus, only one matrix inversion of B is required.
These equations are known as the fast-decoupled power flow equations and this is most commonly used as the power flow solver in commercial packages.

## Slide 67: Part 1 - Review of balanced power flow
Review of balanced power flow
  Gauss Iterative Technique
  Gauss-Seidel Iterative Technique
  Newton Raphson
  Fast Decoupled
  DC Power Flow

## Slide 68: DC Power Flow
DC powerflow is a non-iterative solution because of various assumptions.
  Reactive power flows are ignored.
  All node voltages are assumed to be 1 per unit.
  The entire problem reduced to a single set of linear equations:
      P
The name DC Power Flow is derived from the fact that the equations are linear and the solution of the equations is real power.
DC Power Flow is used in Optimal Power Flow (OPF) solvers, Location Marginal Price (LMP) solvers, and Contingency Analysis (CA).

## Slide 69: Part 2 - Forward Backward Sweep (FBS) Method
If the distribution feeders are mainly radial (which is true in most cases), the iterative techniques discussed above for transmission networks show poor convergence characteristics.
Instead, an iterative technique called Forward Backward Sweep is used for radial distribution systems.
Consider Figure 7 as shown in the next slide. It is a nonlinear system with constant complex power loads.

## Slide 70: Forward Backward Sweep (FBS) Method
The ‘Forward’ sweep computes the voltage at node 5 under no-load condition.
With no load currents, there are no line currents.
Thus the node 5 voltage will equal that of the specified source voltage.
The ‘Backward’ sweep commences by computing the load current at node 5.

## Slide 71: Forward Backward Sweep (FBS) Method
In general, the load current at each node is computed by:
    (59)
The backward sweep will determine a computed source voltage .
However, the first iteration will produce a voltage that is not equal to the specified source voltage .
Because the system is non-linear, the solution must be found by again doing an iteration of the ‘Forward’ sweep.

## Slide 72: Forward Backward Sweep (FBS) Method
The ‘Forward’ sweep is conducted with the specified source voltage and the line currents from the previous backward sweep.
Using KVL for the loop between node 1 and node 2 gives:
    (60)
    This procedure is repeated for each line segment until a “new” voltage is determined at node 5.
    Using the new voltage a backward sweep is started that will lead to a new computed voltage at the source.

## Slide 73: Forward Backward Sweep (FBS) Method
    The forward and backward sweep process is continued until the difference between the computed and specified voltage at the source is within a given tolerance.
Example
Figure 8 shows a single-phase lateral with line impedance Ω/mile.
The impedance of Segment 1-2 is
Ω.
The impedance of Segment 2-3 is
Ω.

## Slide 74: Forward Backward Sweep (FBS) Method
Example (Continued)
The loads are:
(kW + j kVAr)
The source voltage at node 1 is 7,200 volts.
The first forward sweep computes node 3 voltage as:
The backward sweeps starts by computing load current at node 3:
A

## Slide 75: Forward Backward Sweep (FBS) Method
Example (Continued)
The current flowing in Section 2-3 is A.
Then the voltage at node 2 is computed:
V
The load current at node 2 is:
A
The current in segment 1-2 is A
The voltage at source node 1 is computed:
V

## Slide 76: Forward Backward Sweep (FBS) Method
Example (Continued)
Now compare the magnitude of computed node 1 voltage to the magnitude of specified source voltage.
V
If error is less than specified tolerance, solution is achieved.
Typical error tolerance is .0001 per-unit, thus for 7200 V is 7.2 V.
Because 176.2 7.2, forward sweep begins by setting voltage at node 1 to specified source voltage: V.

## Slide 77
Forward Backward Sweep (FBS) Method
Example (Continued)
Now compute voltage at node 2 using value of node 1 voltage and computed line current from previous backward sweep.
V
Continue the Forward sweep by computing the next downstream voltage. Currents computed in previous backward sweep are used in forward sweep.
V
Now repeat backward sweep starting with newly computed voltage at node 3.

## Slide 78: Forward Backward Sweep (FBS) Method
    General Feeder
    For a general feeder like the one shown, the following methodology is adopted.
    For the forward sweep, using the specified voltage at node 1, compute the voltages at the “end” nodes (6, 8, 9, 11 and13)
    The backward sweep is first conducted from the “end” nodes to the “junction” nodes. “Junction” nodes in this case would be node 10 for nodes 11, 12; node 7 for nodes 8 and 9; node 5 for nodes 7 and 6 and finally node 4 for nodes 10, 5 and 7.

## Slide 79: Forward Backward Sweep (FBS) Method
    General Feeder (Continued)
    The downstream “junction” node voltages are first calculated before moving to the upstream “junction” nodes. For example, in this case, voltage at node 7 is calculated before node 5; node 10 voltage is calculated before calculating voltage at node 4.
    The backward sweep is completed with the calculation of the voltage at node 1 and compared with the specified source voltage.
    If the comparison is not within tolerance, a forward sweep is again conducted using new upstream voltages and the current from the previous backward sweep.

## Slide 80: Forward Backward Sweep (FBS) Method
    General Feeder (Continued)
    The forward sweep is completed when new end voltages are found.
    A backward sweep is started with the new end voltages.
    Continue the forward and backward sweeps until the calculated voltage at the source is within the specified tolerance of the source voltage.
    Thus all the node voltages and line currents are obtained in this way.

## Slide 81: Forward Backward Sweep (FBS) Method
    For the unbalanced feeder analysis on the feeder shown, the feeder can be broken into “series” and “shunt” components.
    Series Components will be Line Segments, Transformers and Voltage Regulators.
    Shunt components will be Spot static loads, Spot induction machines, Distributed Loads and Capacitor Banks.
    Using the generalized matrices, the voltage drops can be computed.

## Slide 82: Forward Backward Sweep (FBS) Method
    It is extremely important that the impedances and admittances of the line segments are computed using the exact spacing and phasing.
    Because of the unbalanced loading and resulting unbalanced line currents, the voltage drops due to the mutual coupling of the lines becomes very important.

## Slide 83: Forward Backward Sweep (FBS) Method
    An unbalanced feeder example

## Slide 84: Forward Backward Sweep (FBS) Method
Starting with an assumed or known voltage calculate the current consumed by each load in the system.
Node 634 load: Phase a: 160 kW 110 kVar
Phase b: 120 kW 90 kVar
Phase c: 120 kW 90 kVar
Assume: Phase Va: 2401+0j
Phase Vb: -1200-2080j
Phase Vc: -1200+2080j
Yields: Ia= 66.6-45.8j
Ib= -57.4-24.6j
Ic= 7.5+62.0j
Given: I=(S/V)*

## Slide 85: Forward Backward Sweep (FBS) Method
Sum the currents at each node in the system until the current at the source is determined.
Ia= 66.6-45.8j
Ib= -57.4-24.6j
Ic= 7.5+62.0j

## Slide 86: Forward Backward Sweep (FBS) Method
Using the calculated currents determine the voltage drops on each segment.
Since the voltage drop is dependent on the load of the other phases a complete per phase calculation must be used.

## Slide 87: Forward Backward Sweep (FBS) Method
Based on the new voltages recalculate the new current draw of each load and perform another sweep.
Using the calculated currents determine the voltage drops on each segment.
Since the voltage drop is dependent on the load of the other phases a complete per phase calculation must be used.

## Slide 88: Part 3 - Three Phase Current Injection (TCIM) Newton Raphson (NR) method
This method uses power flow formulations based on current injections.
The current injections are split into real and reactive components.
The set of nonlinear equations that results is solved using the Newton Raphson method.

## Slide 89: TCIM-NR
Three phase current mismatches for bus are:
where
Bus is directly connected to bus
is the nodal admittance bus matrix element.
(61)

## Slide 90: TCIM-NR
The specified active and reactive powers at bus for phase are:
where , , , are the active and reactive powers, respectively, of generators and loads.
The effect of voltage level on system loads is represented by second order polynomial equations, as follows:
where , are constant power components, , are constant current components, , are constant impedance components of phase load at bus , and .
(62)
(63)

## Slide 91: TCIM-NR
Express Eq. (61) in terms of its real and imaginary parts:
(65)
(64)

## Slide 92: TCIM-NR
Apply Newton’s method to (64) and (65).
where .
The off-diagonal elements are identical to the corresponding elements of the bus admittance matrix.
(66)

## Slide 93: TCIM-NR
The current mismatch of (66) for bus and phase can be expressed:
(67)

## Slide 94: TCIM-NR
where active and reactive power mismatches given by:
where
(68)
(69)

## Slide 95: TCIM-NR
The system of linear equations in (66) are solved for the voltage increments using sparse matrix techniques using the Tinney-2 ordering scheme.
At each iteration, the voltages are updated.
where
(70)

## Slide 96: TCIM-NR
Representing PV Buses
  Assume a PV bus is directly connected to buses and .
  Then Eq (66) can be expressed:
(71)

## Slide 97: TCIM-NR
Where each ; is a 6x6 sub-matrix.
Since both the diagonal and off-diagonal elements of column of (71) are functions of real and imaginary voltages, the Jacobian matrix will have to be updated at every iteration.
Three-phase current mismatches at bus are given by:
=
=
(72)

## Slide 98: TCIM-NR
Powerful feature of TCIM comes from the fact that the Jacobian matrix has partitions that are identical to the bus admittance matrix.
Algorithm:
  Initialize the iteration count and set voltages to initial value.
  Compute three-phase active and reactive power injections (Eq’s 69).
  Compute power mismatches (Eq’s 68).
  Test for convergence: if max and max then finish, else go to next step.
  Compute Jacobian matrix.
  Solve (71) for voltage increments.
  Update voltages (70), then go to Step 2.

## Slide 99: Substation and Distribution Automation
Conclusion of Module 3: Distribution level power flow