## Slide 1: Energy Storage and Electric Vehicles Module 7

## Slide 2: Energy Storage and Electric Vehicles Module Outline
Part 1: General Information
  Background
  Forms of energy storage
  Deployments of energy storage
Part 2: Energy Storage Uses
  Peak shifting
  Generation shifting
  Ancillary Services
Part 3: Electric Vehicles
  Impacts on distribution grid
  Usage potential
  Storage considerations
  Implementation issues

## Slide 3: Part 1: General Information
Background
Forms of Energy Storage
  Chemical Storage
  Physical Storage
Deployments of Energy Storage
  Grid Tied
  Grid Influencing

## Slide 4: Background
Electric load continues to grow, and generation and transmission capabilities are becoming unable to meet these new demands.
Environmental and economic concerns often make generation and transmission creation difficult to accomplish.
“Modern Grid” and “Smart Grid” applications look at incorporating new technologies and communication systems to more efficiently operate the system, as opposed to increasing capacity.

## Slide 5: Background (continued)
Energy storage technology can help enhance system reliability, aid power transfer, and maintain power quality.
Ideally, Energy Storage Technology could:2
  Be means to rapidly damp oscillations
  Respond to sudden load changes
  Supply load during transmission or distribution interruptions
  Supply load outside of ideal generation hours
  Correct load voltage profiles with rapid reactive power control
  Allow generators to balance load at their normal speed

## Slide 6: Forms of Energy Storage
Chemical Storage
  Electrochemical processes (batteries)
Physical Storage
  Fluids
  Momentum
  Heat
  Electric fields

## Slide 7: Chemical Energy Storage
Batteries are one of the most cost-effective storage technologies available
Become charged by undergoing internal chemical reactions, and discharge when reversing the reaction
Cannot operate at high power levels for long time periods
Battery lifetime reduced in accordance with frequency of deep discharges
Environmental concerns because of chemicals involved
  Storage and disposal of hazardous materials can cause issues
Battery types:
Sodium Sulfur (NaS)
Lithium Ion (Li-ion)
Lead-Acid (L/A)
Zinc Bromine (ZnBr)
Vanadium Redox
Nickel Cadmium (NiCd)
Nickel Metal Hydride (NiMH)

## Slide 8
Battery Technologies 3
High power output
High efficiency
Good cycle life
Low maintenance
Commercially immature
Sodium Sulfur (NaS)
www.technoologyreview.com
High energy density
Recycled/Reused PHEV batteries
Rapidly developing technology
Relatively expensive
Low cycle life
Lithium Ion (Li-ion)
www.greencar.com
3. Jason’s Slides

## Slide 9
Battery technologies3
Commercially very mature
Low cost of installation
Low conversion efficiency
Very poor cycle life
Low energy density
Lead-Acid (L/A)
www.sbsbattery.com
Easy relocation
Commercially immature
Medium cycle life
Medium cost
Larger footprint
Zinc Bromine (ZnBr)
www.wikipedia.org
3. Jason’s Slides

## Slide 10
Battery technologies3
Nickel Cadmium (NiCd)
Nickel Metal Hydride (NiMH)
Other Technologies
Fast load response
High efficiency
Good cycle life
Commercially immature
Low energy density
Vanadium Redox Battery
www.flikr.com
3. Jason’s Slides

## Slide 11: Physical Energy Storage: Fluid Storage
Pumped Hydro4: Pumped Hydro plants store and generate energy by moving water between reservoirs at different elevations.
When electricity demand is low, water is pumped to the upper reservoir, then during high electricity demand, water is released into the lower reservoir through turbines which generate energy.
4. http://hydro.org/tech-and-policy/technology/pumped-storage/

## Slide 12: Physical Energy Storage: Fluid Storage
Compressed Air (CAES)5: Energy is stored when air is compressed, cooled, and stored at high pressure in a sealed container. That stored energy is converted back to electricity by using the compressed air in a turbine.
Compressed air is stored
in underground caverns
http://en.wikipedia.org/wiki/File:Minebw.jpg
5. Taylor, J.; Halnes, A.; , "Analysis Of compressed air energy storage," PCIC Europe 2010 Conference Record , vol., no., pp.1-5, 15-17 June 2010

## Slide 13: Physical Energy Storage: Momentum
Flywheel1:
Storage system where energy is stored in the kinetic energy of a rotating mass– a rotor that converts energy between electrical and mechanical forms.
In the flywheel system, the rotor operates in a vacuum.
Steel-rotor systems rely mostly on mass of rotor, while composite (resin/glass or resin/carbon-fiber) flywheels rely more on speed.
Advantages:
  Minimal operation and maintenance (O&M) requirements
  Compact and self-contained
  No hazardous chemicals or flammable gasses
Disadvantages:
  Challenges related to rotating energy equipment– site selection, material selection and testing
1. Boyes, J.D.; Clark, N.H.; , "Technologies for energy storage. Flywheels and super conducting magnetic energy storage," Power Engineering Society Summer Meeting, 2000. IEEE , vol.3, no., pp.1548-1550 vol. 3, 2000

## Slide 14: Physical Energy Storage: Heat
Ice Energy: Ice is produced during times of low energy demand, and then used to air condition the building during times of higher energy demand.
Molten Salt6:
In a concentrating solar power plant, thermal energy is stored in the molten salt, then passes through a heat exchanger to create superheated steam, which generates electricity via a turbine.
6. Dunn, R. I.; Hearps, P. J.; Wright, M. N.; , "Molten-Salt Power Towers: Newly Commercial Concentrating Solar Storage," Proceedings of the IEEE , vol.PP, no.99, pp.1-12, 0 doi: 10.1109/JPROC.2011.2163739

## Slide 15: Physical Energy Storage: Electric & Magnetic Fields
Superconducting Magnetic1:
Has a coil of superconducting wire that the direct current flows through, creating the magnetic field that stores the energy without converting it to chemical or mechanical forms.
Must operate at cryogenic temperatures to stay superconductive
Advantages:
  Can both release large quantities of power and fully recharge quickly, thus is efficient and economical
  Highly mobile devices
  No hazardous chemicals or flammable gasses
Disadvantages:
  Produce large magnetic fields
  Potential to rapidly pressurize if coils become non-superconducting
1. Boyes, J.D.; Clark, N.H.; , "Technologies for energy storage. Flywheels and super conducting magnetic energy storage," Power Engineering Society Summer Meeting, 2000. IEEE , vol.3, no., pp.1548-1550 vol. 3, 2000

## Slide 16: Physical Energy Storage: Electric & Magnetic Fields
Ultracapacitors7:
Stores energy electrostatically by physically separating positive & negative charges—unlike batteries which do so chemically.
Advantages:
Very fast charge and discharge times
Long operational life– may be charged and
discharged hundreds of thousands of times
High efficiency
Environmentally friendly
Disadvantages:
Low specific energy
Commercially immature
http://www.nrel.gov/vehiclesandfuels/energystorage/ultracapacitors.html
7. http://www.ultracapacitors.org/index.php?option=com_content&Itemid=57&id=37&task=view

## Slide 17: Deployments of Energy Storage: Grid Tied
Transmission
  NaS
  NiMH/Li-ion
  Pumped Hydro
  Compressed Air
Uses
  Renewable integration
    Reconcile intermittency in power generation
  Short-term backup
  Fast response load pickup
  Grid stabilization
http://en.wikipedia.org/wiki/File:Grid_energy_storage.png

## Slide 18: Deployments of Energy Storage: Grid Tied
Distribution
  Community Energy Storage
    NiMH/Li-ion
    Secondary use of PHEV batteries
Uses
  Demand/generation shifting
  Renewables integration
  Short-term backup
  Fast load pickup

## Slide 19
What is Community Energy Storage (CES)?
www.aeptechcentral.com
www.icandoitmyself.com
3. Jason’s Slides

## Slide 20
Why Community Energy Storage?
Advances in battery technology are beginning to make it cost effective
Enhancement of distributed / renewable generation support
Incentives are being provided by government and utilities
Reduced equipment costs / deferral of system upgrades
Improved reliability and temporary islanding support
Peak shaving / congestion management
Provides power directly to the load
Load response to market signals
Reduced system losses
Power quality control
Local voltage control
www.aeptechcentral.com
3. Jason’s Slides

## Slide 21: Community Energy Storage: Electric Vehicles
Battery types
  NiMH
  Li-ion
Uses
  Same as community energy storage
  Transmission-level benefits – ability to provide regulation capabilities
Differences from other community energy storage
  Availability
  Customer constraints (charging needs, etc.)

## Slide 22: Deployments of Energy Storage: “Grid Influencing”
Ice Energy Storage
  Distribution level
  Tied into HVAC units
  Uses
    Demand shifting/peak reduction
      Customer peak Utility peak
Molten Salt Storage
  Typically transmission level
  Tied to solar-thermal plants or waste-heat producers
  Uses
    Off-peak power production
    Power output stabilization (Renewables Integration)
http://www.ice-energy.com
http://ec.europa.eu/energy/res/sectors/solar_thermal_power_en.htm

## Slide 23: Part2: Energy Storage Uses
Distribution Level
    Peak Shifting
    Ancillary Services
        Regulation
        Load Following

## Slide 24: Energy Storage Uses Distribution Level: Peak Shifting
Purposes
  Reducing customer load during “expensive” power periods
  Reducing customer load during peak utility periods
  Possible carbon impacts  extremely region/instance dependent
Implementations include:
  Thermal Energy Storage
  Community Energy Storage

## Slide 25: Energy Storage Uses Distribution Level: Peak Shifting – Example
Shift energy consumption from high demand time to low demand time
“Valley Filling”

## Slide 26: Energy Storage Uses Distribution Level: Ancillary Services
Distribution-level deployment, but transmission-level benefits
Aggregated populations, or single installations
Regulation and load-following abilities

## Slide 27: Ancillary Services: Regulation
Necessary Capabilities
  Fast charge/discharge (4 seconds)
  Varying power output levels
  Not necessarily large capacity
  Smooth intermittent power from renewables integration
Devices
  Batteries
    CES
    Renewables-integration (smooth localized renewables)
    PHEVs
  Flywheel
  Pumped Hydro or Compressed Air (Small scale theoretically possible, but not practical so far)

## Slide 28: Ancillary Services: Load Following
Necessary Capabilities
  Medium charge/discharge response time (minutes)
  Varying power output levels
  Larger capacity
Devices
  Batteries
    CES
    PHEVs  Not necessarily as well suited
  Pumped Hydro  Small scale theoretically possible, but not practical so far
  Compressed Air  Small scale theoretically possible, but not practical so far

## Slide 29: Ancillary Services: Example
Regulation
Fast variations
Load Following
Slow variations
Base Load
Constant

## Slide 30: Part 3: Electric Vehicles
Overview
Electric Vehicles on the Distribution Grid
Usage Potentials
Storage Considerations
Implementation Issues

## Slide 31: Electric Vehicles – Overview
History
Classifications of Electric Vehicles
  Hybrid Electric Vehicle
  Plug-in Hybrid Electric Vehicle
  Battery Electric Vehicle
Examples
  HEV
  PHEV
  BEV
Current Deployment

## Slide 32: Electric Vehicles – History[ref2,ref3]
Electric vehicles began as early as 1830’s
  Thomas Davenport – small drifter – 1835
  Robert Davidson – electric locomotive – 1838
  Robert Anderson – electric carriage (1830s – exact date unknown)
Late 19th/Early 20th century
Late 19th/Early 20th century
  1897 – electric taxis in New York city
  Wood’s Phaeton – horseless carriage – 1902
  Edison’s Detroit Electric Vehicle – 1907 to 1929
Detroit Edison 1916[REF1]

## Slide 33: Electric Vehicles – History[ref2,ref3]
1920s – 1990s
  Decline in electric vehicles
    Interstate system required longer range
    Mass production made cheaper gas engines (Henry Ford)
    Discovery of crude oil deposits made gasoline cheaper
    Invention of the electric starter (Kettering – 1912)
  Some experiments persisted
    Zagato Zele / Elcar – 1975
    Sebring-Vanguard CitiCar – 1974 – 1977
    Lunar Roving Vehicle – 1971/1972
Lunar Roving Vehicle[ref6]
Elcar[ref5]
CitiCar[ref4]

## Slide 34: Electric Vehicles – History[ref2,ref3]
1990s
  California Air Resources Board (CARB) mandate for “zero emissions vehicles”
    General Motors EV1
    Toyota RAV4
    General Motors S10 EV
    Honda EV Plus
    Chrysler TEVan
  CARB mandate modified
    Most vehicles destroyed by manufacturers
    328 RAV4s sold to public
GM EV1[ref9]
Honda EV Plus[ref8]
Toyota RAV4 EV[ref7]

## Slide 35: Electric Vehicles – History[ref2,ref3]
Late 1990’s to Present
  Renewed interest
    Battery technology has improved
    Petroleum prices risen
    Increased public interest in “sustainability”
    Reliable Plug-in Hybrid Electric Vehicle technology
  Production vehicles becoming available
    Tesla Roadster
    Nissan Leaf
    Chevrolet Volt
    Toyota Prius

## Slide 36: Electric Vehicles – Classifications
Hybrid Electric Vehicle (HEV)
  Combustion engine and electric motor both present
  Battery only chargeable via regenerative braking and combustion engine
Plug-in Hybrid Electric Vehicle (PHEV)
  Combustion engine and electric motor both present
  Battery chargeable through regenerative braking, combustion engine, and via external electrical source (plug)
Battery Electric Vehicle/Electric Vehicle (BEV)
  No combustion engine
  Battery chargeable via regenerative braking and external electrical source

## Slide 37: Electric Vehicles – Hybrid Electric Vehicle
Toyota Prius
Honda Insight
Ford Fusion Hybrid
Ford Fusion Hybrid[ref11]
Toyota Prius[ref10]
Honda Insight[ref12]

## Slide 38: Electric Vehicles – Plug-in Hybrid Electric Vehicle
Chevrolet Volt
Toyota Prius PHEV
BYD F3DM
BYD F3DM[ref15]
Chevrolet Volt[ref13]
Toyota Prius PHEV[ref14]

## Slide 39: Electric Vehicles – Battery Electric Vehicle
Nissan Leaf
Mini Cooper Mini-E
Tesla Roadster
Tesla Roadster[ref18]
Nissan Leaf[ref16]
Mini Cooper Mini-E[ref17]

## Slide 40: Electric Vehicles – Current Deployment[ref19]
Electric Vehicle Numbers
  27,000 – Estimated number on the road (2011)
  496,000 – Expected number by 2015
Batteries
  Li-ion chemistry in most
  Capacities vary
    Toyota Prius PHEV – 4.4 kWh
    Nissan Leaf – 24 kWh
    Chevrolet Volt – 16 kWh
    Mini Cooper Mini-E – 35 kWh
If 2015 numbers and Chevy Volt battery sizes are used, the grid ideally has access to almost 8 GWh of storage!
Even a small fraction of this is a significant resource for the power grid.

## Slide 41: Electric Vehicles on the Distribution Grid
Potential loading issues
  Can be equivalent load to an extra hot water heater in the house
    Level 1 Charging – 120 VAC @ 16 A = 1.92 kW
    Level 2 Charging – 240 VAC @ 32 A = 7.68 kW
    240 VAC @ 80 A = 19.2 kW
  Distribution system effects
    Coincidental loading – commuters all plugging in when come home
    Potential to overload distribution transformers
    Possible peak generation issues
  Solutions
    Time-of-use rates for charging
    Deferred (timer-based) charging
    Regulation charging
Varying resources
  Different size batteries
  Different capabilities
    Adjustable charging rates
    Limited by hardware or battery management systems
    Ability to charge, maybe ability to discharge

## Slide 42: Usage Potential
Overview
Off-peak Storage
Ancillary Services

## Slide 43: Usage Potential – Overview
Electric vehicles as a grid resource
  Potential as load (V2GHalf or G2V)
    Charge rate can be varied to meet grid demands
    “Load resource” availability dictated by charge needed
  Potential as storage (V2GFull or V2G)
    Charge rate and discharge rate can be varied to meet grid demands
    Ability to discharge after 100% full – maintain longer “grid resource” availability
Electric vehicles as a customer item
  Battery capacity
    Spontaneous trips
    “Charge by” requirements
  Compensation for use as grid resource
  Control location
    Localized
    Centralized
V2GHalf or G2V
V2GFull or V2G

## Slide 44: Usage Potential – Off-peak Storage
V2G required
Direct Economics
  Charge electric vehicle during cheaper night rates
  Sell back into grid when prices higher
  Feed load from electric vehicle battery
Distributed Renewable Generation
  Charge during generation peak
    Solar peak – daytime charging
    Wind peak – often nighttime charging
  Utilize during periods of low generation
Grid Stability
  Charge during excess generation
  Provide back into grid during generation shortfalls

## Slide 45: Usage Potential – Ancillary Services
Type of service
  Regulation – Fast response time – on the order of 4 seconds
  Load following – Slow response time – on the order of 1 to 5 minutes
External control or frequency-based
V2G
  Provide both “incremental” and “decremental” power to the grid
  Incremental – charge for over-frequency/over-generation
Regulation Services – Balancing[ref20]
Charging follows balancing requirements
  Decremental – discharge for under-frequency/under-generation
  Ability to maintain availability by discharging after 100% state-of-charge
G2V or V2GHalf
  Provide mainly “incremental” power, but supply “apparent decremental”
  Incremental – charge for over-frequency/over-generation
  Apparent decremental – slow/stop charge rate for under-frequency/under-generation
  Resource unavailable once 100% state-of-charge reached

## Slide 46: Storage Considerations
Availability Constraints
Customer Requirements
Life Cycle
Battery “Second life” Usage

## Slide 47: Storage Considerations – Availability Constraints
Electric vehicles need storage for transportation – not always plugged into the charging station
Customer may have unexpected trips that cause “available” resource to become spontaneously “unavailable”
Local distribution constraints (congestion) may dictate the “availability” of an electric vehicle as storage

## Slide 48: Storage Considerations – Customer Requirements
Electric vehicle is a vehicle as a first use – customer may want certain levels of charge by certain times
  Dictates charging/discharging rates
  Determines resource availability
Customer may override “storage-mode” charging
  Pure charging of battery – no grid services
  If expected as part of aggregation, will alter estimates
Customer may only connect when charging – no idle connections
  Limits availability of electric vehicle as resource
  Limits flexibility on charging scenarios due to time constraints

## Slide 49: Storage Considerations – Life Cycle
Potential life cycle influences
  Extra charge/discharge cycles associated with grid use may shorten the life of the battery
  Shallow discharge/charge cycles of regulation services may limit battery life
  Excess cycling causing thermal considerations (overheating)
Overall effects
  Limit battery life as a “traction” battery
  Voiding of battery/automotive warranty
  Extra cycles on charging/discharging equipment

## Slide 50: Storage Considerations – “Second Life” Usage
Batteries “unfit” for transportation usage still have significant capacity
Useful for community energy storage projects
  Smaller (backyard or pad placement)
  “Safe” – built for automotive use, so various containment/safety mechanisms in place
Reduces environmental impact of batteries by extending their useful life
Incentives to customers
  Deals with utility/automotive manufacturers to recoup costs
  On-site energy storage

## Slide 51: Implementation Issues
Availability/Customer Requirements
Hardware Location
Novelty

## Slide 52: Implementation Issues – Availability/Customer Requirements
Availability dictated by when car is plugged in and has free charge capacity
  Range anxiety may force “charge now” option always
  Vehicle may not be connected when not charging – limits potential for emergency grid usage
  Shorter commutes and constant charging may naturally limit electric vehicle as a resource
Customer travel expectations
  Certain battery capacity by certain time (“charge by”) – drives overall charge/discharge cycle
  Spontaneous trips – capacity to take these trips expected
Customer ownership
  Incentives for usage of their vehicle
  Relinquishment of control over charging (if centrally aggregated)
  Additional wear and tear on battery and components

## Slide 53: Implementation Issues – Hardware Location
Storage usage control
  Centrally located
    Communications channel to aggregator
    Additional hardware to handle communications
  Decentralized
    Cheaper, local hardware
    Not as coordinated
Local hardware location
  Electric Vehicle Supply Equipment
    Not located on car
    Higher infrastructure costs
    Location tied, not vehicle tied
  Electric Vehicle
    Located on car
    Higher vehicle costs
    Follows vehicle – if appropriate service is available
  Split
    Higher costs on both sides
    Communications over charging cable or some other medium

## Slide 54: Implementation Issues – Novelty
Electric vehicles relatively new to modern market
  Range anxiety issues most prevalent fear – manufacturers want to avoid anything that may augment this fear
    Vehicle fails to meet 100% state-of-charge due to excess grid needs
    Long discharge cycle occurs right before “spontaneous” trip
    Limit impacts on battery that may shorten range/life
  Create overall positive experience towards electric vehicles
    Interview process to determine “understanding candidates” – Leaf and Mini-E
    Limit factors to alter this experience – use as storage device introduces unknowns
Electric vehicles typically more expensive that gasoline counterparts
  Additional “storage-capable” hardware increases price
  Utility incentives may offset, but not always available

## Slide 55: Sources
[1] Boyes, J.D.; Clark, N.H.; , "Technologies for energy storage. Flywheels and super conducting magnetic energy storage," Power Engineering Society Summer Meeting, 2000. IEEE , vol.3, no., pp.1548-1550 vol. 3, 2000 doi: 10.1109/PESS.2000.868760 URL: http://ieeexplore.ieee.org/stamp/stamp.jsp?tp=&arnumber=868760&isnumber=18790
[2] Ribeiro, P.F.; Johnson, B.K.; Crow, M.L.; Arsoy, A.; Liu, Y.; , "Energy storage systems for advanced power applications," Proceedings of the IEEE , vol.89, no.12, pp.1744-1756, Dec 2001 doi: 10.1109/5.975900 URL: http://ieeexplore.ieee.org/stamp/stamp.jsp?tp=&arnumber=975900&isnumber=21066
[3] Jason’s Slides

## Slide 56
[4] http://hydro.org/tech-and-policy/technology/pumped-storage/
[5] Taylor, J.; Halnes, A.; , "Analysis Of compressed air energy storage," PCIC Europe 2010 Conference Record , vol., no., pp.1-5, 15-17 June 2010 URL: http://ieeexplore.ieee.org/stamp/stamp.jsp?tp=&arnumber=5525746&isnumber=5525727
[6] Dunn, R. I.; Hearps, P. J.; Wright, M. N.; , "Molten-Salt Power Towers: Newly Commercial Concentrating Solar Storage," Proceedings of the IEEE , vol.PP, no.99, pp.1-12, 0 doi: 10.1109/JPROC.2011.2163739 URL: http://ieeexplore.ieee.org/stamp/stamp.jsp?tp=&arnumber=6035949&isnumber=4357935
[7] http://www.ultracapacitors.org/index.php?option=com_content&Itemid=57&id=37&task=view

## Slide 57: Sources
[4] http://hydro.org/tech-and-policy/technology/pumped-storage/
[5] Taylor, J.; Halnes, A.; , "Analysis Of compressed air energy storage," PCIC Europe 2010 Conference Record , vol., no., pp.1-5, 15-17 June 2010 URL: http://ieeexplore.ieee.org/stamp/stamp.jsp?tp=&arnumber=5525746&isnumber=5525727
[6] Dunn, R. I.; Hearps, P. J.; Wright, M. N.; , "Molten-Salt Power Towers: Newly Commercial Concentrating Solar Storage," Proceedings of the IEEE , vol.PP, no.99, pp.1-12, 0 doi: 10.1109/JPROC.2011.2163739 URL: http://ieeexplore.ieee.org/stamp/stamp.jsp?tp=&arnumber=6035949&isnumber=4357935
REF1, Asterion, “Detroit Electric 1916”, Wikipedia, Dec. 2006, URL: http://en.wikipedia.org/wiki/File:Detroit_Electric_1916.jpg
REF2, Wikipedia contributors, "History of the electric vehicle," Wikipedia, //en.wikipedia.org/w/index.php?title=History_of_the_electric_vehicle&oldid=454559473 (accessed October 12, 2011)
REF3, Department of Energy – Energy Efficiency & Renewable Energy, “History of Electric Vehicles,” URL: http://www1.eere.energy.gov/vehiclesandfuels/avta/light_duty/fsev/fsev_history.html, (accessed October 12, 2011)
REF4, D0li0, “Citicar”, Wikipedia, URL: http://en.wikipedia.org/wiki/File:Citicar.jpg
REF5, Mike Chancey, “Harry van Soolen’s 1974 Zagato Elcar”, Sept. 25, 2010, URL: http://evalbum.com/1832
REF6, NASA – Eric M. Jones, “Apollo 15 Map and Image Library”, Aug 29, 2011, URL: http://www.hq.nasa.gov/office/pao/History/alsj/a15/images15.html
REF7, George Manning, “Toyota RAV4 EV”, March 2001, URL: http://en.wikipedia.org/wiki/File:Toyota_RAV_4_EV.jpg
REF8, Evplus, “1997-1999 Honda EV Plus”, Aug 2007, URL: http://en.wikipedia.org/wiki/File:1997-1999_Honda_EV_Plus_02.jpg
REF9, Claus Ableiter, “General Motors EV1”, Oct 2008, URL: http://en.wikipedia.org/wiki/File:General_Motors_EV1_im_Museum_Autovision.jpg
REF10, IFCAR, “2004-2008 Toyota Prius”, Jun 2008, URL: http://en.wikipedia.org/wiki/File:2nd_Toyota_Prius.jpg
REF11, Mario Roberto Duran Ortiz, “2010 Ford Fusion Hybrid promotional vehicle”, Jan 2010, URL: http://en.wikipedia.org/wiki/File:2010_Ford_Fusion_Hybrid_WAS_2010_8962.JPG
REF12, 本人撮影, “Honda Insight Back”, Jul 2007, URL: http://en.wikipedia.org/wiki/File:Honda_Insight_Back.JPG
REF13, Mario Roberto Duran Ortiz, “2011 Chevrolet Volt”, Jan 2010, URL: http://en.wikipedia.org/wiki/File:Chevrolet_Volt_WAS_2010_8852.JPG
REF14, Mario Roberto Duran Ortiz, “Toyota Prius Plug-In Hybrid demonstration vehicle”, Jul 2011, URL: http://en.wikipedia.org/wiki/File:BOS_07_2011_Prius_PHEV_ZipCar_2830.jpg
REF15, Anthonares, “BYD F3DM plug-in hybrid”, URL: http://en.wikipedia.org/wiki/File:Byd_f3_dm.jpg
REF16, Richard Kelly, “Nissan Leaf ‘Glacier Pearl’ White”, Oct 2010, URL: http://en.wikipedia.org/wiki/File:Nissan_LEAF_Glacier_Pearl_White.jpg
REF17, Bill Bicholls, “Electric MINI”, Feb 2010, URL: http://en.wikipedia.org/wiki/File:An_Electric_MINI_-_geograph.org.uk_-_1710621.jpg
REF18, Plug In America, “Tesla Roadster electric car”, May 2008, URL: http://en.wikipedia.org/wiki/File:Tesla_Roadster_electric_car_DSC_0160.jpg
REF19, Kim Hill and Joshua Cregger, “Deployment Rollout Estimate of Electric Vehicles 2011-2015”, Center for Automotive Research, Jan 2011, URL: http://www.cargroup.org/pdfs/deployment.pdf
REF20, Francis Tuffner and Michael C. W. Kintner-Meyer, “Using Electric Vehicles to Meet Balancing Requirements Associated with Wind Power,” PNNL-20501 Report. Pacific Northwest National Laboratory. Richland, WA, July 2011.