## Slide 1: Substation and Distribution Automation
Module 3: Distribution level power flow

## Slide 2: Module 3 Overview
Part 1 - Review of balanced power flow
Part 2 - Forward Backward Sweep (FBS) method
Part 3 - Three Phase Current Injection (TCIM) Newton Raphson (NR) method

## Slide 3: Part 1 - Review of balanced power flow
Review of balanced power flow
  Gauss Iterative Technique
  Gauss-Seidel Iterative Technique
  Newton Raphson
  Fast Decoupled
  DC Power Flow

## Slide 4: Review of balanced power flow
Fig. 1 Four bus system: One-line diagram
The net complex power injected into the bus is given by:
where complex power supplied by the generator is:
and the complex power drawn by the loads is:
(1)
(2)
(3)

## Slide 5
  Review of balanced power flow
Fig. 4 Power network of Fig. 3 lumped and redrawn
Fig. 3 Equivalent power system circuit

## Slide 6
The network model of Fig. 3 has been redrawn in Fig. 4 after lumping the shunt admittances at the buses.
  Review of balanced power flow
The real and reactive powers injected into the th bus are then:
(4)
(5)

## Slide 7
Besides the ground node, there are four other nodes (buses) at which the current from the sources is injected into the network.
  Review of balanced power flow
Apply Kirchhoff’s current law (KCL) at nodes 1,2,3 and 4, respectively, to get the following four equations:
(6)

## Slide 8
Rearranging and writing in matrix form gives:
  Review of balanced power flow
(7)

## Slide 9
Above equation (7) can be recognized to be of the standard form:
(7)
(8)

## Slide 10
Each off-diagonal term Yik (I, k = 1,2,3,4) is the mutual admittance (transfer admittance) between nodes i and k and equals the negative of the sum of all admittances connected directly between these nodes.
Further, Yik = Yki
Each admittance Yii (i = 1,2,3,4) is called the self admittance (or driving point admittance) of node i and equals the algebraic sum of all the admittances terminating on the node.
  Review of balanced power flow
Figure 4

## Slide 11
(8)
From index notation, Eq. (8) can be written in compact form as:
(9)
or, in matrix form:
(10)
where YBUS denotes the matrix of bus admittance and is known as bus admittance matrix.
The dimension of the YBUS matrix is (n × n) where n is the number of buses.
The total number of nodes are m = n + 1 including the ground (reference) node.
  Review of balanced power flow

## Slide 12
Load Flow Problem:
The complex power injected by the source into the ith bus of a power system is:
where Vi is the voltage at the th bus with respect to ground and Ii is the source current injected into the bus.
(11)
The load flow problem is handled more conveniently by use of Ii rather than Ii*.
  Review of balanced power flow

## Slide 13
Therefore, taking the complex conjugate of Eq. (11) gives:
(12)
Substitute from Eq. (9) to get:
(13)
  Review of balanced power flow

## Slide 14
Equating real and imaginary parts:
In polar form:
  Review of balanced power flow
(14)
(15)
(16)

## Slide 15
Real and reactive powers can now be expressed as:
(17)
  Review of balanced power flow
(18)

## Slide 16
Equations (17) and (18) represent 2n power flow equations at n buses of a power system (n real power flow equations and n reactive power flow equations).
Each bus is characterized by four variables; , , and , resulting in a total of 4n variables.
Equations (17) and (18) can be solved for 2n variables if the remaining 2n variables are specified.
Pi (real power) =
(17)
Qi (reactive power) =
(18)
Power flow equations
  Review of balanced power flow

## Slide 17
Practical considerations allow a power system analyst to fix a priori two variables at each bus.
The solution for the remaining 2n bus variables is obtained by iterative numerical techniques.
  Review of balanced power flow
Power flow equations (continued)
Depending upon which two variables are specified, the buses are classified into three categories – PQ Buses (Load Buses), PV Buses (Generator Buses), Slack or Reference Bus.
Slack bus (ref. bus) - Voltage magnitude and angle known - ,
PV Bus : real power and voltage magnitude known - ,
PQ Bus : real and reactive powers known - ,

## Slide 18
When we solve the power flow problem, all the variables must lie within practical limits.
Voltage magnitude must satisfy the inequality:
(19)
  Review of balanced power flow
(ii) Certain of the ’s must satisfy the inequality constraint:
(20)
(iii) Because of physical limitations on the generators, PGi and QGi are
constrained as follows:
(21)
(22)

## Slide 19
The total generation of real and reactive power must equal the total load demand plus losses, i.e.
where PL and QL are system real and reactive power loss, respectively
(23)
(24)
  Review of balanced power flow

## Slide 20: Part 1 - Review of balanced power flow
Review of balanced power flow
  Gauss Iterative Technique
  Gauss-Seidel Iterative Technique
  Newton Raphson
  Fast Decoupled
  DC Power Flow

## Slide 21: Gauss Iterative Technique
Given ,,…… , we need to find ,,…… .
Knowing , ……, it is possible to find . Since is already known, only , ……, need to be found. These unknowns may be found from the equations of (26).
Taking the complex conjugate, replace (25) and (26) by:
(26)
(25)
(27)

## Slide 22: Gauss Iterative Technique
Dividing (27) by and separating out the term, (27) can be rewritten as:
  or, rearranging:
(28)
(29)

## Slide 23: Gauss Iterative Technique
Thus, we get implicit nonlinear algebraic equations in the unknown complex in the form:
where the are given by (29).
The numbering of (30) can be changed such that =, =.
(30)

## Slide 24: Gauss Iterative Technique
In vector notation, (30) is written in the form :
(31)
Solving (31) by iteration we get
(32)
  where the superscript indicates the iteration number.
Thus, starting with an initial value , a sequence of , , ……are generated until convergence is achieved.

## Slide 25: Gauss Iterative Technique
In practice, the iterations are stopped when the changes in become very small.
T is the Euclidean norm
Thus, Gauss iteration, v = 0,1,2,…..:
(33)

## Slide 26: Part 1 - Review of balanced power flow
Review of balanced power flow
  Gauss Iterative Technique
  Gauss-Seidel Iterative Technique
  Newton Raphson
  Fast Decoupled
  DC Power Flow

## Slide 27: Gauss-Seidel Iterative Technique
Recall: Gauss iteration, v = 0,1,2,…..:
When is being solved, would be known. Since is a better estimate than , the updated value is used.
Similarly, when solving for , then and can be used. This modification is called the Gauss-Seidel iteration.
(33)

## Slide 28: Gauss-Seidel Iterative Technique
Gauss-Seidel iteration, v = 0,1,2,…..:
(34)

## Slide 29: Part 1 - Review of balanced power flow
Review of balanced power flow
  Gauss Iterative Technique
  Gauss-Seidel Iterative Technique
  Newton Raphson
  Fast Decoupled
  DC Power Flow

## Slide 30: Newton Raphson Method
Newton-Raphson Methods were originally developed for use on transmission level analysis.
They are based on the power injections at each node, both real and reactive.
These power injections are then used to update the voltage and voltage angle.
The NR method is a powerful method of solving a system of non-linear algebraic equations, requiring the calculation and inversion of a Jacobian matrix, which is computationally intensive.
It is faster and converges in most cases.
It is the most widely used method for solving power flow problem.

## Slide 31
Consider a set of non-linear algebraic equations:
(35)
Assume initial values of unknowns as , ,…, .
Let , ,…, be the corrections, which upon being added to the initial guess, give the actual solution.
Therefore:
(36)
Newton-Raphson Method
The NR method in its general form:

## Slide 32
Expanding these equations in Taylor series around the initial guess gives:
where , are the derivatives of fi with respect to x1, x2, …., xn evaluated at .
Newton-Raphson Method
(37)

## Slide 33
Neglecting higher order terms, write the above Eq. in matrix form.
Newton-Raphson Method
Equation 37:
(38)

## Slide 34
Equation 38 can also be expressed as:
(39)
is known as the Jacobian matrix (obtained by differentiating the function vector f with respect to x and evaluating it at x0)
Equation (39) can be rearranged:
(40)
Newton-Raphson Method

## Slide 35
Approximate values of corrections can be obtained from Eq. (40). These being a set of linear algebraic equations that can be solved efficiently by traingularization and back substitution.
For the th iteration:
(41)
Iterations are continued till Eq. (35) is satisfied to any desired accuracy, i.e.
(42)
Newton-Raphson Method
Equation 40:

## Slide 36: Newton-Raphson Method
Pi is the real power injection at node
Qi is the reactive power injection at node
Gik is real portion of the admittance between node and
Bik is imaginary portion of the admittance between node and
Vi is the voltage magnitude at node
i is the voltage angle at node
Applying to a power system
(43)

## Slide 37: Newton-Raphson Method
Consider Eq’s 43 re-written:
such that and are functions of , with being the vector of ’s, and the vector of ’s.
The vector f(x) may be expressed
where is the vector of ’s, and the vector of ’s.
(44)
Applying to a power system (continued)

## Slide 38: Newton-Raphson Method
Recall Eq. 40:
.
Thus
where the jacobian matrix
Applying to a power system (continued)
(45)

## Slide 39
Transmission level worked examples
            Gauss-Siedel
            Newton-Raphson

## Slide 40: Gauss-Seidel Iterative Technique
Example A: Gauss-Seidel Power Flow
Figure 5 shows a single-line diagram of a five-bus power system. The four tables on the following slides contain input data.
Figure 5

## Slide 41
Bus | Type | V per unit | degrees | per unit | per unit | per unit | per unit | per unit | per unit
1 | Swing | 1.0 | 0 | - | - | 0 | 0 | - | -
2 | Load | - | - | 0 | 0 | 8 | 2.8 | - | -
3 | Constant Voltage | 1.05 | - | 5.2 | - | .8 | .4 | 4 | -2.8
4 | Load | - | - | 0 | 0 | 0 | 0 | - | -
5 | Load | - | - | 0 | 0 | 0 | 0 | - | -
Bus | Type | V per unit |  |  |  |  |  |  | 
1 | Swing | 1.0 | 0 | - | - | 0 | 0 | - | -
2 | Load | - | - | 0 | 0 | 8 | 2.8 | - | -
3 | Constant Voltage | 1.05 | - | 5.2 | - | .8 | .4 | 4 | -2.8
4 | Load | - | - | 0 | 0 | 0 | 0 | - | -
5 | Load | - | - | 0 | 0 | 0 | 0 | - | -
Table 1: Bus input Data for Example A
Bus 1 has a generator connected and is a swing bus.
Bus 3 has a generator and a load connected. It is a voltage controlled bus.
Buses 2,3, and 5 are all load buses.

## Slide 42
Bus-to-Bus | R’ per unit | X’ per unit | G’ per unit | B’ per unit | Maximum MVA per unit
2-4 | 0.0090 | 0.100 | 0 | 1.72 | 12.0
2-5 | 0.0045 | 0.050 | 0 | 0.88 | 12.0
4-5 | 0.00225 | 0.025 | 0 | 0.44 | 12.0
Bus-to-Bus | R per unit | X per unit | per unit | per unit | Maximum MVA per unit | Maximum TAP Setting per unit
1-5 | 0.00150 | 0.02 | 0 | 0 | 6.0 | -
3-4 | 0.00075 | 0.01 | 0 | 0 | 10.0 | -
Bus-to-Bus | R per unit | X per unit |  |  | Maximum MVA per unit | Maximum TAP Setting per unit
1-5 | 0.00150 | 0.02 | 0 | 0 | 6.0 | -
3-4 | 0.00075 | 0.01 | 0 | 0 | 10.0 | -
Table 2: Line input Data for Example A
Table 3: Transformer input Data for Example A

## Slide 43
Bus | Input Data | Unknowns
1 |  | 
2 |  | 
3 |  | 
4 |  | 
5 |  | 
Bus | Input Data | Unknowns
1 |  | 
2 |  | 
3 |  | 
4 |  | 
5 |  | 
Table 4: Input Data and Unknowns for Example A
Now compute the elements of the second row of
Since buses 1 and 3 are not directly connected to bus 2,

## Slide 44
By using values from Table 2, compute the following.
per unit
per unit
per unit

## Slide 45
Note that half the shunt admittance of each line connected to bus 2 is included in , and the other half is at the other end of these lines.
Nodal equations for the power system network may now be written as
.
For each load bus, is calculated by
  .
Applying the Gauss-Seidel power flow method to the nodal equations, with as expressed above, gives
The above equation can be applied twice during each iteration, first using , then replacing that by on the right side.

## Slide 46
For a voltage-controlled bus, is unknown, but can be calculated from the following.
Now, use Gauss-Seidel to calculate the phasor voltage at load bus 2 after the first iteration ().
per unit

## Slide 47
Now recalculate using = in place of .
per unit
After performing computations at buses 3, 4, and 5, the first Guess-Seidel iteration will be complete.

## Slide 48: Newton-Raphson Example
(Transmission Level Example)

## Slide 49: Newton Raphson Procedure
(Example Continued)
(46)
(47)
(48)

## Slide 50: Newton Raphson Procedure
(Example Continued)
(49)
(50)

## Slide 51: N-R Power Flow Results
(Example Continued)

## Slide 52: Part 1 - Review of balanced power flow
Review of balanced power flow
  Gauss Iterative Technique
  Gauss-Seidel Iterative Technique
  Newton Raphson
  Fast Decoupled
  DC Power Flow

## Slide 53: Fast Decoupled Power Flow
As described above, the Jacobian Matrix can be expressed as
The values of the off-diagonal sub-matrices and are small and can be approximated to zero.
Hence, the power flow problem can be decoupled.
(51)

## Slide 54: Fast Decoupled Power Flow
Substitute approximations into Eq. (48).
Then,
(52)

## Slide 55: Fast Decoupled Power Flow
Further assumptions can be made about the terms in and .
Usually the terms of the are smaller than the and can be ignored.
All per unit bus voltage magnitudes are considered approximately equal and difference between bus angles are considered small.

## Slide 56: Fast Decoupled Power Flow
Then, the diagonal terms of and can be written as:
(53)
(54)

## Slide 57: Fast Decoupled Power Flow
The off-diagonal terms of and can be written as:
(55)

## Slide 58
Consider and ,
where B may obtained from by stripping away the first row and column and then taking the imaginary part.
Then,
Fast Decoupled Power Flow
(56)

## Slide 59
Substitute into Eq. 52 to get:
Because of the assumption that all per unit are equal, assume the second in (57) is the identity matrix.
Thus
Note that and are just scaled versions of and .
Fast Decoupled Power Flow
(57)
(58)

## Slide 60: Fast Decoupled Power Flow
An important observation is that B is a constant matrix, independent of iteration count. Thus, only one matrix inversion of B is required.
These equations are known as the fast-decoupled power flow equations and this is most commonly used as the power flow solver in commercial packages.

## Slide 61: Part 1 - Review of balanced power flow
Review of balanced power flow
  Gauss Iterative Technique
  Gauss-Seidel Iterative Technique
  Newton Raphson
  Fast Decoupled
  DC Power Flow

## Slide 62: DC Power Flow
If from the above the reactive power flow equations are completely ignored and all voltages are assumed at 1p.u., the power flow solution becomes a linear, convergent set of real power equation of the form
      P
The name DC Power Flow is derived from the fact that the equations are linear and the solution of the equations is real power.
DC Power Flow is used in OPF solvers, LMP solvers and Contingency analysis.

## Slide 63: Part 2 - Forward Backward Sweep (FBS) method
If the distribution feeders are mainly radial (which is true in most cases), the iterative techniques discussed above for transmission networks show poor convergence characteristics.
Instead, an iterative technique called Forward Backward Sweep is used for radial distribution systems.
Consider Figure 7 as shown in the next slide. It is a nonlinear system with constant complex power loads.

## Slide 64: Part 2 - Forward Backward Sweep (FBS) method
The ‘Forward’ sweep computes the voltage at node 5 under no-load condition.
With no load currents, there are no line currents.
Thus the node 5 voltage will equal that of the specified source voltage.
The ‘Backward’ sweep commences by computing the load current at node 5.
Figure 7: Nonlinear Ladder Network

## Slide 65: Part 2 - Forward Backward Sweep (FBS) method
In general, the load current at each node is computed by:
    (59)
The backward sweep will determine a computed source voltage .
However, the first iteration will produce a voltage that is not equal to the specified source voltage .
Because the system is non-linear, the solution must be found by again doing an iteration of the ‘Forward’ sweep.

## Slide 66: Part 2 - Forward Backward Sweep (FBS) method
The ‘Forward’ sweep is conducted with the specified source voltage and the line currents from the previous backward sweep.
Using KVL at node 2 gives:
    (60)
    This procedure is repeated for each line segment until a “new” voltage is determined at node 5.
    Using the new voltage a backward sweep is started that will lead to a new computed voltage at the source.

## Slide 67: Part 2 - Forward Backward Sweep (FBS) method
    The forward and backward sweep process is continued until the difference between the computed and specified voltage at the source is within a given tolerance.
Figure 8
Example
Figure 8 shows a single-phase lateral with line impedance Ω/mile.
The impedance of Segment 1-2 is
Ω.
The impedance of Segment 2-3 is
Ω.

## Slide 68: Part 2 - Forward Backward Sweep (FBS) method
Example (Continued)
The loads are:
(kW + j kVAr)
The source voltage at node 1 is 7,200 volts.
The first forward sweep computes node 3 voltage as:
The backward sweeps starts by computing load current at node 3:
A

## Slide 69: Part 2 - Forward Backward Sweep (FBS) method
Example (Continued)
The current flowing in Section 2-3 is A.
Then the voltage at node 2 is computed:
V
The load current at node 2 is:
A
The current in segment 1-2 is A
The voltage at source node 1 is computed:
V

## Slide 70: Part 2 - Forward Backward Sweep (FBS) method
Example (Continued)
Now compare the magnitude of computed node 1 voltage to the magnitude of specified source voltage.
V
If error is less than specified tolerance, solution is achieved.
Typical error tolerance is .0001 per-unit, thus for 7200 V is 7.2 V.
Because 176.2 7.2, forward sweep begins by setting voltage at node 1 to specified source voltage: V.

## Slide 71
Part 2 - Forward Backward Sweep (FBS) method
Example (Continued)
Now compute voltage at node 2 using value of node 1 voltage and computed line current from previous backward sweep.
V
Continue the Forward sweep by computing the next downstream voltage. Currents computed in previous backward sweep are used in forward sweep.
V
Now repeat backward sweep starting with newly computed voltage at node 3.

## Slide 72: Part 2 - Forward Backward Sweep (FBS) method
    General Feeder
    For a general feeder like the one shown in Figure 9, the following methodology is adopted.
    For the forward sweep, using the specified voltage at node 1, compute the voltages at the “end” nodes (6, 8, 9, 11 and13)
    The backward sweep is first conducted from the “end” nodes to the “junction” nodes. “Junction” nodes in this case would be node 10 for nodes 11, 12; node 7 for nodes 8 and 9; node 5 for nodes 7 and 6 and finally node 4 for nodes 10, 5 and 7.
Figure 9

## Slide 73: Part 2 - Forward Backward Sweep (FBS) method
    General Feeder (Continued)
    The downstream “junction” node voltages are first calculated before moving to the upstream “junction” nodes. For example, in this case, voltage at node 7 is calculated before node 5; node 10 voltage is calculated before calculating voltage at node 4.
    The backward sweep is completed with the calculation of the voltage at node 1 and compared with the specified source voltage.
    If the comparison is not within tolerance, a forward sweep is again conducted using new upstream voltages and the current from the previous backward sweep.

## Slide 74: Part 2 - Forward Backward Sweep (FBS) method
    General Feeder (Continued)
    The forward sweep is completed when new end voltages are found.
    A backward sweep is started with the new end voltages.
    Continue the forward and backward sweeps until the calculated voltage at the source is within the specified tolerance of the source voltage.
    Thus all the node voltages and line currents are obtained in this way.

## Slide 75: Part 2 - Forward Backward Sweep (FBS) method
    For the unbalanced feeder analysis, as shown in Figure 10, the feeder can be broken into “series” and “shunt” components.
    Series Components will be Line Segments, Transformers and Voltage Regulators.
    Shunt components will be Spot static loads, Spot induction machines, Distributed Loads and Capacitor Banks.
    Using the generalized matrices, the voltage drops can be computed.
Figure 10

## Slide 76: Part 2 - Forward Backward Sweep (FBS) method
    It is extremely important that the impedances and admittances of the line segments are computed using the exact spacing and phasing.
    Because of the unbalanced loading and resulting unbalanced line currents, the voltage drops due to the mutual coupling of the lines becomes very important.

## Slide 77: Part 2 - Forward Backward Sweep (FBS) method
    An unbalanced feeder example

## Slide 78: Part 2 - Forward Backward Sweep (FBS) method
Starting with an assumed or known voltage calculate the current consumed by each load in the system.
Node 634 load: Phase a: 160 kW 110 kVar
Phase b: 120 kW 90 kVar
Phase c: 120 kW 90 kVar
Assume: Phase Va: 2401+0j
Phase Vb: -1200-2080j
Phase Vc: -1200+2080j
Yields: Ia= 66.6-45.8j
Ib= -57.4-24.6j
Ic= 7.5+62.0j
Given: I=(S/V)*

## Slide 79: Part 2 - Forward Backward Sweep (FBS) method
Sum the currents at each node in the system until the current at the source is determined.
Ia= 66.6-45.8j
Ib= -57.4-24.6j
Ic= 7.5+62.0j

## Slide 80: Part 2 - Forward Backward Sweep (FBS) method
Using the calculated currents determine the voltage drops on each segment.
Since the voltage drop is dependent on the load of the other phases a complete per phase calculation must be used.

## Slide 81: Part 2 - Forward Backward Sweep (FBS) method
Based on the new voltages recalculate the new current draw of each load and perform another sweep.
Using the calculated currents determine the voltage drops on each segment.
Since the voltage drop is dependent on the load of the other phases a complete per phase calculation must be used.

## Slide 82: Part 3 - Three Phase Current Injection (TCIM) Newton Raphson (NR) method
This method uses power flow formulations based on current injections.
The current injections are written in rectangular coordinates.
The set of nonlinear equations that results is solved using the Newton Raphson method.

## Slide 83: Part 3 - Three Phase Current Injection (TCIM) Newton Raphson (NR) method
Three phase current mismatches for bus are:
where
Bus is directly connected to bus
is the nodal admittance bus matrix element.
(61)

## Slide 84: Part 3 - Three Phase Current Injection (TCIM) Newton Raphson (NR) method
The specified active and reactive powers at bus for phase are:
where , , , are the active and reactive powers, respectively, of generators and loads.
The effect of voltage level on system loads is represented by second order polynomial equations, as follows:
where , are constant power components, , are constant current components, , are constant impedance components of phase load at bus , and .
(62)
(63)

## Slide 85: Part 3 - Three Phase Current Injection (TCIM) Newton Raphson (NR) method
Express Eq. (61) in terms of its real and imaginary parts:
(65)
(64)

## Slide 86: Part 3 - Three Phase Current Injection (TCIM) Newton Raphson (NR) method
Apply Newton’s method to (64) and (65).
where .
The off-diagonal elements are identical to the corresponding elements of the bus admittance matrix.
(66)

## Slide 87: Part 3 - Three Phase Current Injection (TCIM) Newton Raphson (NR) method
The current mismatch of (66) for bus and phase can be expressed:
(67)

## Slide 88: Part 3 - Three Phase Current Injection (TCIM) Newton Raphson (NR) method
where active and reactive power mismatches given by:
where
(68)
(69)

## Slide 89: Part 3 - Three Phase Current Injection (TCIM) Newton Raphson (NR) method
The system of linear equations in (66) are solved for the voltage increments using sparse matrix techniques using the Tinney-2 ordering scheme.
At each iteration, the voltages are updated.
where
(70)

## Slide 90: Part 3 - Three Phase Current Injection (TCIM) Newton Raphson (NR) method
Representing PV Buses
  Assume a PV bus is directly connected to buses and .
  Then Eq (66) can be expressed:
(71)

## Slide 91: Part 3 - Three Phase Current Injection (TCIM) Newton Raphson (NR) method
Where each ; is a 6x6 sub-matrix.
Since both the diagonal and off-diagonal elements of column of (71) are functions of real and imaginary voltages, the Jacobian matrix will have to be updated at every iteration.
Three-phase current mismatches at bus are given by:
=
=
(72)

## Slide 92: Part 3 - Three Phase Current Injection (TCIM) Newton Raphson (NR) method
Powerful feature of TCIM comes from the fact that the Jacobian matrix has partitions that are identical to the bus admittance matrix.
Algorithm:
  Initialize the iteration count and set voltages to initial value.
  Compute three-phase active and reactive power injections (Eq’s 69).
  Compute power mismatches (Eq’s 68).
  Test for convergence: if max and max then finish, else go to next step.
  Compute Jacobian matrix.
  Solve (71) for voltage increments.
  Update voltages (70), then go to Step 2.

## Slide 93: Sources
[1]Vyakaranam, B. Chapter 6: Power Flows [PowerPoint Slides] for EEC 473/571 Power Systems, Cleveland State University, Department of Electrical and Computer Engineering. 2009.
[2] Bergen, A.R.; Vittal V. Power Systems Analysis, Second Edition. Upper Saddle River (NJ): Prentice-Hall, Inc; 2000. 619p.
[3] Kersting, W.H., Distribution System Modeling and Analysis. Boca Raton: CRC Press; 2002. 314p.
[4] Garcia, P.A.N.; Pereira, J.L.R.; Carneiro, S., Jr.; da Costa, V.M.; Martins, N.; , "Three-phase power flow calculations using the current injection method," Power Systems, IEEE Transactions on , vol.15, no.2, pp.508-514, May 2000 [5] “Book with Gauss-Seidel Power flow example”
[6] “Newton Raphson Example”

## Slide 94: Module 3 Concluding Comments
1
2
3
4