## Slide 1: Substation and Distribution Automation
Module 2: Modeling of distribution level components

## Slide 2: Module 1 Overview
Part 1: Overhead Lines
Part 2: Underground lines
Part 3: Three Phase Transformer Models
Part 4: Center –Tapped Transformers and Secondaries
Part 5: IEEE Test Systems

## Slide 3: Part 1: Overhead Lines
Series impedance of Overhead Lines
  Transposed Three-phase Lines
  Untransposed Distribution Lines
  Carson’s Equations
  Modified Carson’s Equations
  Primitive Impedance Matrix for Overhead Lines
  Phase Impedance Matrix for Overhead Lines
  Sequence Impedances
  Parallel Overhead Distribution Lines
Shunt Admittance of Overhead Parallel Lines
General Voltage Drop Equation (examples from Kevin)

## Slide 4
Series impedance of Overhead Lines
Critical step before the analysis of the distribution feeder can begin.
Resistance component of the conductors is typically taken from a look-up table (can be found in Appendix A of the text book)
The reactance comes from the inductive reactance (self and mutual) of the conductors. The inductive reactance is due to the magnetic field surrounding the conductors.

## Slide 5
Series impedance of Overhead Lines
Figure 1.0 shows magnetic flux lines created by currents flowing through conductors to (current is flowing outwards here)
Figure 1.0

## Slide 6
It is further assumed the sum of the currents will be zero. That is
(1)
The total flux linking the conductor is given by:
W-T/m (2)
where: Distance between conductor and conductor (ft.)
= Geometric Mean Radius of conductor (ft.)
Series impedance of Overhead Lines (Contd…)

## Slide 7
Series impedance of Overhead Lines (Contd…)
Inductance is given by the flux linkage divided by the current.
Thus, the inductance of the conductor consists of the “self inductance” of the conductor and the “mutual inductance” between conductor and the other conductors.
Self Inductance: H/m (3)
Mutual Inductance: H/m (4)

## Slide 8: Part 1: Overhead Lines
Series impedance of Overhead Lines
  Transposed Three-phase Lines
  Untransposed Distribution Lines
  Carson’s Equations
  Modified Carson’s Equations
  Primitive Impedance Matrix for Overhead Lines
  Phase Impedance Matrix for Overhead Lines
  Sequence Impedances
  Parallel Overhead Distribution Lines
Shunt Admittance of Overhead Parallel Lines
General Voltage Drop Equation

## Slide 9
Series impedance of Overhead Lines
Transposed Three-phase Lines
Usual assumptions made for High-Voltage Transmission lines:
    Transposed – Each phase occupies the same physical position on the structure for one-third of the length of the line.
    Balanced Loading – All phases are equally loaded.
Hence “self” and “mutual” inductance terms can be combined into one “phase” inductance.
The series impedance per phase of a transposed three-phase line consisting of one conductor per phase is given by:
Series Impedance: Ω/mile (5)

## Slide 10: Part 1: Overhead Lines
Series impedance of Overhead Lines
  Transposed Three-phase Lines
  Untransposed Distribution Lines
  Carson’s Equations
  Modified Carson’s Equations
  Primitive Impedance Matrix for Overhead Lines
  Phase Impedance Matrix for Overhead Lines
  Sequence Impedances
  Parallel Overhead Distribution Lines
Shunt Admittance of Overhead Parallel Lines
General Voltage Drop Equation

## Slide 11
Untransposed Distribution Lines
Distribution Systems consist of single-phase, two-phase and untransposed three-phase lines serving unbalanced loads.
Hence it is necessary to retain the identity of the self and mutual impedance terms of the conductors in addition to taking into account the ground return path for the unbalanced currents.
The resistance of the conductors is taken directly from the table of conductor data.
Series impedance of Overhead Lines (Contd…)

## Slide 12
Untransposed Distribution Lines
Equations (3) and (4) are used to calculate self and mutual reactances of the conductors.
  Recall:
Series impedance of Overhead Lines (Contd…)
H/m (3)
H/m (4)

## Slide 13
Untransposed Distribution Lines
Assumptions
  Inductive reactance will be at a frequency of 60 Hz.
  Length of the conductor is one mile.
The self and mutual impedances are given by
Series impedance of Overhead Lines (Contd…)
Ω/mile (6)
Ω/mile (7)

## Slide 14
Two Conductors with Dirt Return
Figure 2.0

## Slide 15
Two Conductors with Dirt Return
Voltage between conductor and ground (using Kirchhoff’s Voltage Law):
(8)
Collect terms and use:
(from KVL) (9)
to get:
(10)
where:
(11)
(12)

## Slide 16
Primitive Circuit Impedances
Series impedance of Overhead Lines (Contd…)
Figure 3.0

## Slide 17
Primitive Circuit Impedances
Series impedance of Overhead Lines (Contd…)
(13)
(14)
Substitute the self and mutual impedance equations:
Ω/mile (6)
Ω/mile (7)
into our “hat” impedances (eq’s 11 and 12)
to get the primitive self and mutual impedances:

## Slide 18: Part 1: Overhead Lines
Series impedance of Overhead Lines
  Transposed Three-phase Lines
  Untransposed Distribution Lines
  Carson’s Equations
  Modified Carson’s Equations
  Primitive Impedance Matrix for Overhead Lines
  Phase Impedance Matrix for Overhead Lines
  Sequence Impedances
  Parallel Overhead Distribution Lines
Shunt Admittance of Overhead Parallel Lines
General Voltage Drop Equation

## Slide 19
Carson’s Equations
Because distribution is inherently unbalanced, the most accurate analysis should not make any assumptions regarding :
  the spacing between conductors
  conductor sizes
  transposition
Carson assumes the earth is an infinite, uniform solid, with a flat uniform upper surface and a constant resistivity.
Any “end effects” introduced at the neutral grounding points are not large at power frequencies, and there, are neglected.
Series impedance of Overhead Lines (Contd…)

## Slide 20
Carson made use of conductor images; that is, every conductor at a given distance above ground has an image conductor at the same distance below-ground.
Series impedance of Overhead Lines (Contd…)
Carson’s Equations
Ω/mile (15)
Ω/mile (16)
Self Impedance:
Mutual Impedance:
Figure 4.0

## Slide 21
Series impedance of Overhead Lines (Contd…)
Carson’s Equations
Variable Definitions
system angular frequency in radians per second
Ω/mile
radius of conductor in feet
system frequency in Hertz
resistivity of earth in Ω-meters
distance between conductors and in feet (see Figure)
distance between conductors and image in feet (see Figure)
angle between a pair of lines drawn from conductor to its own image and to the image of conductor

## Slide 22
Series impedance of Overhead Lines (Contd…)
Carson’s Equations
Variable Definitions (Contd…)
Ω/mile (17)
(18)
(19)
(20)

## Slide 23: Part 1: Overhead Lines
Series impedance of Overhead Lines
  Transposed Three-phase Lines
  Untransposed Distribution Lines
  Carson’s Equations
  Modified Carson’s Equations
  Primitive Impedance Matrix for Overhead Lines
  Phase Impedance Matrix for Overhead Lines
  Sequence Impedances
  Parallel Overhead Distribution Lines
Shunt Admittance of Overhead Parallel Lines
General Voltage Drop Equation

## Slide 24
Modified Carson’s Equations: Derivation
Approximations:
(21)
(22)
Substitute Eq’n 20 (the value of ) into (22) and simplify:
(23)
(24)
(25)
Now simplify the Carson’s Eq’s (substituting in the first):

## Slide 25
Modified Carson’s Equations: Derivation
Substitute expressions for and
(26)
(27)
Now substitute our expression for and values and :
(28)
(29)

## Slide 26
Modified Carson’s Equations
Series impedance of Overhead Lines (Contd…)
Assume:
frequency = 60 Hertz
earth resistivity = 1000 Ohm-meters
Hence the modified Carson’s equations are:
Ω/mile (30)
Ω/mile (31)

## Slide 27
Comparing Equations
Series impedance of Overhead Lines (Contd…)
(13)
(14)
(30)
(31)
Modified Carson’s:
Primitive Impedance:

## Slide 28: Part 1: Overhead Lines
Series impedance of Overhead Lines
  Transposed Three-phase Lines
  Untransposed Distribution Lines
  Carson’s Equations
  Modified Carson’s Equations
  Primitive Impedance Matrix for Overhead Lines
  Phase Impedance Matrix for Overhead Lines
  Sequence Impedances
  Parallel Overhead Distribution Lines
Shunt Admittance of Overhead Parallel Lines
General Voltage Drop Equation

## Slide 29
(32)
Primitive Impedance Matrix for Overhead Lines
The Modified Carson’s Equations (30 & 31) are used to compute the elements of the “primitive impedance matrix”.
The primitive impedance matrix for a three-phase line consisting of neutrals will be of the form:
Series impedance of Overhead Lines (Contd…)

## Slide 30
Primitive Impedance Matrix for Overhead Lines
In partitioned form, Equation (32) becomes:
Series impedance of Overhead Lines (Contd…)
(33)

## Slide 31: Part 1: Overhead Lines
Series impedance of Overhead Lines
  Transposed Three-phase Lines
  Untransposed Distribution Lines
  Carson’s Equations
  Modified Carson’s Equations
  Primitive Impedance Matrix for Overhead Lines
  Phase Impedance Matrix for Overhead Lines
  Sequence Impedances
  Parallel Overhead Distribution Lines
Shunt Admittance of Overhead Parallel Lines
General Voltage Drop Equation

## Slide 32
Phase Impedance Matrix for Overhead Lines
Series impedance of Overhead Lines (Contd…)
For most applications, the primitive impedance matrix needs to be reduced to a 3X3 “phase frame” matrix consisting of the self and mutual equivalent impedances for the three phases. Figure 5.0 shows a four-wire grounded neutral line segment
Figure 5.0

## Slide 33
Phase Impedance Matrix for Overhead Lines (Contd…)
Series impedance of Overhead Lines (Contd…)
= + (34)
Figure 5.0

## Slide 34
Phase Impedance Matrix for Overhead Lines
One standard method of reduction is the “Kron” reduction. The Kron reduction method applies KVL to the circuit.
Series impedance of Overhead Lines (Contd…)
In partitioned form, (34) becomes:
(35)
Because the neutral is grounded, voltages and equal 0.
Thus
(36)
(37)

## Slide 35
Phase Impedance Matrix for Overhead Lines
Series impedance of Overhead Lines (Contd…)
Solve (37) for :
(38)
Substitute (38) into expression (36):
(39)
where
(40)

## Slide 36
After having applied the Kron reduction technique, the final phase impedance matrix becomes:
(41)
Series impedance of Overhead Lines (Contd…)
Phase Impedance Matrix for Overhead Lines
Ω/mile

## Slide 37
Phase Impedance Matrix for Overhead Lines
The phase impedance matrix for a three-wire delta line is determined by the application of Carson’s equations without the Kron reduction step.
The phase impedance matrix can be used to accurately determine the voltage drops on the feeder line segments once the currents have been determined.
Since no approximations (transpositions for example) have been made regarding the spacing between conductors, the effect of the mutual coupling between the phases is accurately taken into account.
Series impedance of Overhead Lines (Contd…)

## Slide 38
Phase Impedance Matrix for Overhead Lines
The application of the Modified Carson’s equations and the phase frame matrix lead to the most accurate model of a line segment as shown in Figure 6.0.
Series impedance of Overhead Lines (Contd…)
Figure 6.0

## Slide 39
Phase Impedance Matrix for Overhead Lines
Series impedance of Overhead Lines (Contd…)
length

## Slide 40: Part 1: Overhead Lines
Series impedance of Overhead Lines
  Transposed Three-phase Lines
  Untransposed Distribution Lines
  Carson’s Equations
  Modified Carson’s Equations
  Primitive Impedance Matrix for Overhead Lines
  Phase Impedance Matrix for Overhead Lines
  Sequence Impedances
  Parallel Overhead Distribution Lines
Shunt Admittance of Overhead Parallel Lines
General Voltage Drop Equation

## Slide 41
Sequence Impedances
Many times the analysis of a feeder will use only the positive and zero sequence impedances for the line segments. There are 2 methods for obtaining these impedances.
The first method uses the Modified Carson’s Equations and the Kron reduction to obtain the phase impedance matrix.
The definition of line-to-ground phase voltages as a function of the line-to-ground sequence voltages is given by
Series impedance of Overhead Lines (Contd…)
(42)
where

## Slide 42
Sequence Impedances
In condensed form Equation (42) becomes:
(43)
  where
(44)
The phase line currents can be defined in the same manner.
(45)
Series impedance of Overhead Lines (Contd…)

## Slide 43
Sequence Impedances
Equation (43) can be used to solve for the sequence line-to-ground voltages as a function of the phase line-to-ground voltages.
(46)
  where:
(47)
Series impedance of Overhead Lines (Contd…)

## Slide 44
The voltage equation in matrix form for the line segment:
can be transformed to the sequence domain by multiplying both sides by and also substituting in the definition of the phase currents as given by Equation (43).
(48)
where:
(49)
Series impedance of Overhead Lines (Contd…)
Sequence Impedances

## Slide 45
Sequence Impedances
  Equation (48) in expanded form is given by
Series impedance of Overhead Lines (Contd…)
Equation (49) is the defining equation for converting phase impedances to sequence impedances. In equation (49), the diagonal terms of the matrix are the sequence impedances of the line such that:
(50)

## Slide 46
Sequence Impedances
<Kevin’s example of sequential components not being equal to phase components. In any commercial tool, often diagonal components are ignored>
Series impedance of Overhead Lines (Contd…)

## Slide 47
Sequence Impedances
The off-diagonal terms of Equation (49) represent the mutual coupling between sequences.
If the lines were transposed, these off-diagonal terms would be zero. This will generally be true for off-diagonal terms.
For transposed lines, the phase impedance matrix is modified so the three diagonal terms are equal, and all of the off-diagonal terms are equal.
Usually, the procedure is to set the three diagonal terms of the phase impedance matrix equal to the average of the diagonal terms of Equation (41) and the off-diagonal terms equal to the average of the off-diagonal terms of Equation (41).
Series impedance of Overhead Lines (Contd…)

## Slide 48
Sequence Impedances for transposed lines
Series impedance of Overhead Lines (Contd…)
Ω/mile (51)
Ω/mile (52)
Ω/mile (52)
Self and Mutual Impedance defined as:
Phase Impedance matrix:

## Slide 49
Sequence Impedances for transposed lines
Series impedance of Overhead Lines (Contd…)
Ω/mile (54)
Ω/mile (55)
Determine Sequence Impedances:

## Slide 50
Sequence Impedances
A second method that is commonly used to determine the sequence impedances directly is to employ the concept of Geometric Mean Distances (GMD).
Series impedance of Overhead Lines (Contd…)
GMD between phases:
(56)
GMD between phases and neutral:
(57)

## Slide 51
Sequence Impedances
Series impedance of Overhead Lines (Contd…)
The above GMD’s are used in the Modified Carson Equations, resulting in:
Ω/mile (58)
Ω/mile (59)
Ω/mile (60)
Ω/mile (61)

## Slide 52: Part 1: Overhead Lines
Series impedance of Overhead Lines
  Transposed Three-phase Lines
  Untransposed Distribution Lines
  Carson’s Equations
  Modified Carson’s Equations
  Primitive Impedance Matrix for Overhead Lines
  Phase Impedance Matrix for Overhead Lines
  Sequence Impedances
  Parallel Overhead Distribution Lines
Shunt Admittance of Overhead Parallel Lines
General Voltage Drop Equation

## Slide 53
    Parallel Overhead Lines
    It is fairly common in a distribution system to find instances where two distribution lines are “physically” parallel.
    The phase impedance matrix of parallel lines is computed from the application of Carson’s equations and the Kron reduction method.
Series impedance of Overhead Lines
Line 1
Line 2
Figure 7.0

## Slide 54
    Parallel Overhead Lines
    With reference to Figure 7.0, the voltage drops in the two lines are given by:
    (62)
    The procedure for computing the phase impendence matrix for parallel underground distribution lines is the same as the parallel overhead lines
Series impedance of Overhead Lines

## Slide 55: Part 1: Overhead Lines
Series impedance of Overhead Lines
  Transposed Three-phase Lines
  Untransposed Distribution Lines
  Carson’s Equations
  Modified Carson’s Equations
  Primitive Impedance Matrix for Overhead Lines
  Phase Impedance Matrix for Overhead Lines
  Sequence Impedances
  Parallel Overhead Distribution Lines
Shunt Admittance of Overhead Parallel Lines
General Voltage Drop Equation

## Slide 56
Shunt Admittance of Overhead Parallel Lines
    General Voltage Drop Equation
    The shunt admittance of a line consists of the conductance and the capacitive susceptance.
    The conductance is usually ignored because it is very small compared to the capacitive susceptance.
    The capacitance of a line is the result of the potential difference between conductors

## Slide 57
Shunt Admittance of Overhead Parallel Lines
    Electric field of a charged round conductor
Figure 8.0

## Slide 58
Shunt Admittance of Overhead Parallel Lines
    Electric field of a charged round conductor
    A charged conductor creates an electric field that emanates outward from the center of the conductor.
    Lines of equipotential are created outward from the center of the conductor.
    A difference of potential between two points is a result of the electric field of the charged conductor.
    When the potential difference between two points is known, then the capacitance between the two points can be computed.

## Slide 59
Shunt Admittance of Overhead Parallel Lines
    General Voltage Drop Equation
(63)
Figure 9.0

## Slide 60: Part 1: Overhead Lines
Series impedance of Overhead Lines
  Transposed Three-phase Lines
  Untransposed Distribution Lines
  Carson’s Equations
  Modified Carson’s Equations
  Primitive Impedance Matrix for Overhead Lines
  Phase Impedance Matrix for Overhead Lines
  Sequence Impedances
  Parallel Overhead Distribution Lines
Shunt Admittance of Overhead Parallel Lines
General Voltage Drop Equation

## Slide 61
Shunt Admittance of Overhead Parallel Lines
    Definition of Terms
permittivity of the medium
permittivity of free space F/meter
relative permittivity of the medium
charge density on conductor cb/meter
distance between conductor and conductor (ft.)
distance between conductor and conductor (ft.)
radius () of conductor

## Slide 62
Shunt Admittance of Overhead Parallel Lines
    Conductors and Images
Figure 10.0

## Slide 63
Shunt Admittance of Overhead Parallel Lines
    The method of conductors and their images is employed in the calculation of the shunt capacitance of overhead lines. This is the same concept that was used for calculating series impedances in the general application of Carson’s Equations.
(64)
when assuming:
(66)
(65)

## Slide 64
Shunt Admittance of Overhead Parallel Lines
    where
The first step is to create the primitive potential coefficient matrix, where the elements of the primitive potential coefficient matrix are given by
distance of the conductor to its image (ft)
distance of the conductor to the image of conductor (ft)
distance of the conductor to conductor (ft)
radius of conductor (ft)
mile/F (67)
mile/F (68)

## Slide 65
Shunt Admittance of Overhead Parallel Lines
    After reducing the primitive potential matrix through Kron reduction, we obtain the potential matrix .
    The shunt capacitance matrix is the inverse of the potential matrix.
(69)
  The Shunt admittance matrix is given by
    (70)
    where

## Slide 66: Part 2: Underground Lines
Underground lines
    Series impedance of Underground Lines
  Concentric Neutral Cable
    Tape Shielded Cables
  Shunt Admittance of Underground Lines
  Concentric Neutral Cable
    Tape Shielded Cables
  Sequence Admittance
  Parallel Underground Distribution Lines
    Series impedance
    Shunt Admittance

## Slide 67: Part 2: Underground Lines
Underground lines
    Series impedance of Underground Lines
  Concentric Neutral Cable
    Tape Shielded Cables
  Shunt Admittance of Underground Lines
  Concentric Neutral Cable
    Tape Shielded Cables
  Sequence Admittance
  Parallel Underground Distribution Lines
    Series impedance
    Shunt Admittance

## Slide 68
  Series impedance of Underground Lines
        Concentric Neutral Cable
      Figure shows the detail of a concentric neutral cable
Figure 11.0

## Slide 69
  Series impedance of Underground Lines
      Concentric Neutral Cable
      In order to apply the Carson’s equations, the following data needs to be extracted from a table of underground cables. (Appendices A and B in the book)
diameter of phase conductor (inches)
nominal diameter over the concentric neutrals of the cable (inches)
diameter of a concentric neutral strand (inches)
geometric mean radius of the phase conductor (feet)
geometric mean radius of a neutral strand (feet)
resistance of the phase conductor (Ω/mile)
resistance of a solid neutral strand (Ω/mile)
number of concentric neutral strands

## Slide 70
  Series impedance of Underground Lines
      Concentric Neutral Cable
      The GMR of the phase conductor and a neutral strand are obtained from the standard table of the conductor data (Appendix A).
      The equivalent GMR of the concentric neutral is computed using the equation
        ft (71)
      where is the radius of a circle passing through the center of the concentric neutral strands given by:
        ft (72)

## Slide 71
      The equivalent resistance of the concentric neutral is:
      Ω/mile (73)
  Series impedance of Underground Lines
      Concentric Neutral Distances
CN to its own phase conductor:
CN to adjacent CN:
Center-to-Center of phase conductors
CN to adjacent phase conductor:
(74)

## Slide 72: Part 2: Underground Lines
Underground lines
    Series impedance of Underground Lines
  Concentric Neutral Cable
    Tape Shielded Cables
  Shunt Admittance of Underground Lines
  Concentric Neutral Cable
    Tape Shielded Cables
  Sequence Admittance
  Parallel Underground Distribution Lines
    Series impedance
    Shunt Admittance

## Slide 73
  Series impedance of Underground Lines (Contd…)
        Tape Shielded Cables
      The tape shielded cable consists of a central conductor covered by a thin layer of non-metallic semi conducting screen to which is bonded the insulating material.
      The insulation is covered by a semiconducting insulation screen. The shield is bare copper tape.
      An insulating jacket encircles the tape shield.

## Slide 74
  Series impedance of Underground Lines (Contd…)
        Tape Shielded Cables
Figure 12.0

## Slide 75
  Series impedance of Underground Lines (Contd…)
      Tape Shielded Cables
      Parameters of the tape shielded cable are:
Modified Carson’s Equations will be applied to calculate:
  self impedances of the phase conductor and the tape shield
  mutual impedance between the phase conductor and the tape shield.
The resistance and GMR of the phase conductor are found in a standard table of conductor data. (Appendix A in this book)
diameter of phase conductor (inches)
outside diameter of the tape shield (inches)
outside diameter over jacket (inches)
thickness of copper tape shield (millimeters)

## Slide 76
  Series impedance of Underground Lines (Contd…)
      Tape Shielded Cables
  The resistance of the tape shield is given by:
      Ω/mile (75)
      Assumptions:
        Temperature is 50 degrees C
        Resistivity is 100 Ω-meter
    The GMR of the tape shield is the radius of a circle passing through the middle of the shield and is given by:
    ft (76)

## Slide 77
  Series impedance of Underground Lines (Contd…)
      Tape Shielded Cables
      The various spacings between a tape shield and the conductors and other tape shields are as follows:
        Tape shield to its own phase:
        radius to midpoint of the shield (feet)
        Tape shield to an adjacent tape shield:
        center-to-center distance of the phase conductors (feet)
        Tape shield to an adjacent phase or neutral conductor:
feet
where center-to-center distance between phase conductors

## Slide 78: Part 2: Underground Lines
Underground lines
    Series impedance of Underground Lines
  Concentric Neutral Cable
    Tape Shielded Cables
  Shunt Admittance of Underground Lines
  Concentric Neutral Cable
    Tape Shielded Cables
  Sequence Admittance
  Parallel Underground Distribution Lines
    Series impedance
    Shunt Admittance

## Slide 79
  Shunt Admittance of Underground Lines
      Concentric Neutral Cable
      Figure shows a basic concentric neutral cable with center conductor being the phase conductor and the concentric neutral strands equally displaced around a circle of radius of Rb
Figure 13.0

## Slide 80
      Concentric Neutral Cable
        where
        = Radius of a circle passing through the centers of the neutral strands
        = Diameter of the phase conductor
        = Diameter of a neutral strand
        = Total number of neutral strands
  Shunt Admittance of Underground Lines

## Slide 81
      Concentric Neutral Cable
    The concentric neutral strands are grounded so that they are all at the same potential.
    Since they are all at the same potential, it is only necessary to determine the potential difference between the phase conductor and strand .
(77)
where
  Shunt Admittance of Underground Lines

## Slide 82
  Shunt Admittance of Underground Lines
      Concentric Neutral Cable
      The voltage drop from the phase conductor to neutral strand is then given by
        (78)
      The electric field of a cable is confined to the insulation material. Cross-Linked Polyethlyene is a very popular insulation material.
      If the minimum value of relative permittivity is assumed, the equation for shunt admittance of the concentric neutral cable is given by
        S/mile (79)

## Slide 83
  Typical Values of Relative Permittivity
        Table 1.0
Material | Relative Permittivity
Polyvinyl Chloride (PVC) | 3.4-8.0
Ethylene-Propylene Rubber (EPR) | 2.5-3.5
Polyethylene (PE) | 2.5-2.6
Cross-Linked Polyethylene (XLPE) | 2.3-6.0

## Slide 84: Part 2: Underground Lines
Underground lines
    Series impedance of Underground Lines
  Concentric Neutral Cable
    Tape Shielded Cables
  Shunt Admittance of Underground Lines
  Concentric Neutral Cable
    Tape Shielded Cables
  Sequence Admittance
  Parallel Underground Distribution Lines
    Series impedance
    Shunt Admittance

## Slide 85
  Shunt Admittance of Underground Lines
(Contd….)
      Tape Shielded Cables
      The tape-shielded cable is shown in Figure 14.0. is the radius of the circle passing through the center of the tape-shield.
Figure 14.0

## Slide 86
  Shunt Admittance of Underground Lines
(Contd….)
      Tape Shielded Cables
      As with the concentric neutral cable, the electric field is confined to the insulation so that the relative permittivity of Table 1.0 will apply.
      The tape-shielded conductor can be visualized as a concentric neutral cable where the number of strands has become infinite.
      Therefore, the equation for the shunt admittance of a tape-shielded conductor becomes:
      S/mile (80)

## Slide 87: Part 2: Underground Lines
Underground lines
    Series impedance of Underground Lines
  Concentric Neutral Cable
    Tape Shielded Cables
  Shunt Admittance of Underground Lines
  Concentric Neutral Cable
    Tape Shielded Cables
  Sequence Admittance
  Parallel Underground Distribution Lines
    Series impedance
    Shunt Admittance

## Slide 88
  Sequence Admittance
      Sequence Admittance of a three phase line
      The sequence admittances of a three-phase line can be determined in much the same manner as the sequence impedances.
      Assume that the 3 X 3 admittance matrix is given in S/mile. Then the three phase capacitance currents as a function of the line-to ground voltages is given by:
(81)
(82)

## Slide 89
  Sequence Admittance
      Sequence Admittance of a three phase line
(83)
(84)
Applying symmetric component transformations:
Sequence admittance matrix given by:

## Slide 90
        Sequence Admittance of a three phase line
    For a three-phase overhead line with unsymmetrical spacing, the sequence admittance matrix will be full (non-zero off diagonal terms).
    However, a three-phase underground line with three identical cables will only have the diagonal terms since there is no “mutual capacitance” between phases.
    In fact, the sequence admittances will be exactly the same as phase admittances.
  Sequence Admittance

## Slide 91: Part 2: Underground Lines
Underground lines
    Series impedance of Underground Lines
  Concentric Neutral Cable
    Tape Shielded Cables
  Shunt Admittance of Underground Lines
  Concentric Neutral Cable
    Tape Shielded Cables
  Sequence Admittance
  Parallel Underground Distribution Lines
    Series impedance
    Shunt Admittance

## Slide 92
    Series Impedance of Parallel Underground Distribution Lines
    The procedure for computing the phase impedence matrix for parallel underground distribution lines is the same as the parallel overhead lines.
    Carson’s equations are applied to find the primitive impedance matrix.
    The Kron reduction is applied to find the final impedance matrix.

## Slide 93: Part 2: Underground Lines
Underground lines
    Series impedance of Underground Lines
  Concentric Neutral Cable
    Tape Shielded Cables
  Shunt Admittance of Underground Lines
  Concentric Neutral Cable
    Tape Shielded Cables
  Sequence Admittance
  Parallel Underground Distribution Lines
    Series impedance
    Shunt Admittance

## Slide 94
Shunt Admittance of Underground Parallel Lines
    Computation of shunt admittance of underground lines is quite simple.
    The electric field created by the charged phase conductor does not link to the adjacent conductors because of the presence of concentric neutrals or the tape shield.
    As a result, the shunt admittance matrix for parallel underground lines will consist of diagonal terms only.

## Slide 95
Shunt Admittance of Underground Parallel Lines
    The diagonal terms for concentric neutral cables are given by:
S/mile (85)
where
radius of circle through center of neutral strands (feet)
radius of the center phase conductor (feet)
radius of neutral strands (feet)
number of neutral strands

## Slide 96
Shunt Admittance of Underground Parallel Lines
    The diagonal terms for tape-shielded cables are given by:
S/mile (86)
where
radius of circle through center of neutral strands (feet)
radius of center of phase conductor (feet)

## Slide 97: Substation and Distribution Automation Module 2
Three Phase Transformer Models
Center –Tapped Transformers and Secondaries
IEEE Test Systems

## Slide 98: Module 1 Overview
Part 1: Overhead Lines
Part 2: Underground lines
Part 3: Three Phase Transformer Models
Part 4: Center –Tapped Transformers and Secondaries
Part 5: IEEE Test Systems

## Slide 99: Part 3: Three Phase Transformer Models
Three Phase Transformer Models
  General Three Phase Transformer Banks
  Generalized Matrices
  Symmetrical Components
  The Delta-Grounded Wye Step Down Connection
  The Ungrounded Wye-Delta Step Down Connection
  The Grounded Wye-Grounded Wye Connection
  The Delta-Delta Connection
  Open Wye-Open Delta
  Thevenin Equivalent Circuit

## Slide 100
    Three-phase transformer banks in the distribution substation transform the transmission or sub-transmission level voltages to the distribution feeder level voltage.
    Different substations transformer connections exist, like the Delta-grounded wye, the delta-delta transformer,… etc.
    The connection used depends on the configuration of the distribution feeder.
  Three Phase Transformer Models

## Slide 101
    Three-phase transformer banks on the feeder will provide the final voltage transformation to the customer’s load.
    Again, different transformer connections can be applied depending on the load characteristics (whether a pure 3 phase load or a combination of single phase and three phase loads).
  Three Phase Transformer Models

## Slide 102
  Quick Review of Wye and Delta Connection
    Figure 1.0: Wye and delta source connections
    Figure 2.0: The line-neutral voltages in terms of the line-line voltages

## Slide 103
    If all the voltages are considered to be positive sequence components (to be discussed later), can be related to as
        (1)
    The reverse relationship also works.
(2)
  Quick Review of Wye and Delta Connection

## Slide 104
  Quick Review of Wye and Delta Connection
    If the voltages considered are negative sequence components (to be discussed later), and can be related as:
(3)
        and
(4)
    The relationship can also be understood by the following.
      (Let )
    (5)
    (6)
    (7)

## Slide 105: Part 3: Three Phase Transformer Models
Three Phase Transformer Models
  General Three Phase Transformer Banks
  Generalized Matrices
  Symmetrical Components
  The Delta-Grounded Wye Step Down Connection
  The Ungrounded Wye-Delta Step Down Connection
  The Grounded Wye-Grounded Wye Connection
  The Delta-Delta Connection
  Open Wye-Open Delta
  Thevenin Equivalent Circuit

## Slide 106
        General Three Phase Transformer Banks
    Figure 3.0 defines the various voltages and currents of all transformer banks with source side ‘’ and load side ‘’.
    The notation is such that upper-case letters refer to the source side and lower-case letters refer to the load side of the bank
  Three Phase Transformer Models
Step-Down Connection:
leads by 30 degrees
leads by 30 degrees
Step-Up Connection:
leads by 30 degrees
leads by 30 degrees
Figure 3.0

## Slide 107
        Generalized Matrices
    The matrix equations for computing the voltages and currents at node as a function of the voltages and currents at node are given by:
(8)
(9)
    The voltages at node as a function of the voltages at node and the currents at node are given by:
    (10)
  Three Phase Transformer Models

## Slide 108: Part 3: Three Phase Transformer Models
Three Phase Transformer Models
  General Three Phase Transformer Banks
  Generalized Matrices
  Symmetrical Components
  The Delta-Grounded Wye Step Down Connection
  The Ungrounded Wye-Delta Step Down Connection
  The Grounded Wye-Grounded Wye Connection
  The Delta-Delta Connection
  Open Wye-Open Delta
  Thevenin Equivalent Circuit

## Slide 109
        Generalized Matrices
    Equation (10) will be used in the forward back sweep method to be described later.
    The matrices and represent the line-to-neutral voltages for an ungrounded wye connection or the line-to-ground voltages for a grounded wye connection.
    For a delta connection, the voltage matrices represent “equivalent” line-to-neutral voltages.
    The current matrices represent the line currents regardless of the transformer winding connection.
  Three Phase Transformer Models

## Slide 110: Part 3: Three Phase Transformer Models
Three Phase Transformer Models
  General Three Phase Transformer Banks
  Generalized Matrices
  Symmetrical Components
  The Delta-Grounded Wye Step Down Connection
  The Ungrounded Wye-Delta Step Down Connection
  The Grounded Wye-Grounded Wye Connection
  The Delta-Delta Connection
  Open Wye-Open Delta
  Thevenin Equivalent Circuit

## Slide 111
    Unbalanced systems cannot be studied in terms of balanced three phase voltages and currents
    Hence the method of symmetrical components is used for unbalanced systems
If the original phasors are voltages, they may be designated Va, Vb, and Vc. The three sets of symmetrical components are designated by the additional subscript 1 for the positive-sequence components, 2 for the negative-sequence components, and 0 for the zero-sequence components
  Quick Review – Symmetrical Components

## Slide 112
    The positive-sequence components of Va, Vb, and Vc are Va1, Vb1, and Vc1, respectively. Similarly, the negative-sequence components are Va2, Vb2, and Vc2, and the zero-sequence components are Va0, Vb0, and Vc0, respectively
Va1
Vc1
Vb1
Va2
Vc2
Vb2
Va0 = Vb0 = Vc0
Positive-sequence
components
Negative-sequence
components
Zero-sequence
components
Fig: Three sets of balanced phasors which are the symmetrical components of three unbalanced phasors
  Quick Review – Symmetrical Components

## Slide 113
Since each of the original unbalanced phasors is the sum of its
components, the original phasors expressed in terms of their components are
The number of unknown quantities can be reduced by expressing
each component of Vb and Vc as the product of Va and some function of the operator
  Quick Review – Symmetrical Components

## Slide 114
  Quick Review – Symmetrical Components
Symmetrical component equations for voltages
matrix form
where

## Slide 115
  Quick Review – Symmetrical Components
Which shows us how to solve three unsymmetrical phasors into their symmetrical components
Similar results apply to line-to-line voltages by replacing Vab, Vbc, and Vca in the above equations

## Slide 116
        Transformers that will be modeled in the coming slides……
        1. The Delta-Grounded Wye Step Down Connection
    Typically used in a distribution substation serving a four-wire wye feeder system.
    Another application is to provide service to a load that is primarily single-phase, since three single-phase circuits are available.
        2. The Ungrounded Wye Delta Connection
    Typically used to provide service to a combination of single-phase “lighting” load and three-phase “power” load such as an induction motor.
  Three Phase Transformer Models

## Slide 117
        Transformers that will be modeled in the coming slides……
  3. The Grounded Wye-Grounded Wye Connection
Primarily used to supply single-phase and three-phase loads on four-wire multigrounded systems.
  4. The Delta-Delta Connection
Primarily used on three-wire delta systems to provide service to a three-phase load or a combination of three-phase and single-phase loads.
  5. Open Wye-Open Delta
Another connection used to supply a combination of single-phase and three-phase loads. Commonly used when the three-phase load is small compared to the single-phase load.
  Three Phase Transformer Models

## Slide 118: Part 3: Three Phase Transformer Models
Three Phase Transformer Models
  General Three Phase Transformer Banks
  Generalized Matrices
  Symmetrical Components
  The Delta-Grounded Wye Step Down Connection
  The Ungrounded Wye-Delta Step Down Connection
  The Grounded Wye-Grounded Wye Connection
  The Delta-Delta Connection
  Open Wye-Open Delta
  Thevenin Equivalent Circuit

## Slide 119
        The Delta-Grounded Wye Step Down Connection
    Typically used in a distribution substation serving a four-wire wye feeder system.
    Another application is to provide service to a load that is primarily single-phase.
    Because of the wye connection, three single-phase circuits are available, making it possible to balance the single phase loading on the transformer bank.
  Three Phase Transformer Models

## Slide 120
        The Delta-Grounded Wye Step Down Connection
  Three Phase Transformer Models
Figure 4.0

## Slide 121
        The Delta-Grounded Wye Step Down Connection
    With reference to Figure 4.0, the line-to-line voltages on the primary side of the transformer connection as a function of the ideal secondary side voltages is:
      (13)
    where is the turns ratio defined as (12)
  Three Phase Transformer Models

## Slide 122
        The Delta-Grounded Wye Step Down Connection
    In condensed form, (13) is
    (14)
    where
    (15)
    To get the line-to-neutral voltages from the line-to-line voltages, we apply the theory of symmetrical components.
  Three Phase Transformer Models

## Slide 123
        The Delta-Grounded Wye Step Down Connection
    The known line-to-line voltages are transformed to their sequence voltages by:
  Three Phase Transformer Models
(16)
where
(17)

## Slide 124
        The Delta-Grounded Wye Step Down Connection
    By definition the zero sequence line-to-line voltage is always zero.
    The relationship between the positive sequence and negative sequence line-to-neutral and line-to-line voltages in matrix form is
    (18)
    (19)
    where (20)
  Three Phase Transformer Models

## Slide 125
        The Delta-Grounded Wye Step Down Connection
    Since the zero sequence line-to-line voltages is zero, the (1,1) term of can be taken as 1.0.
    Knowing the sequence line-to-neutral voltages, the equivalent line-to-neutral voltages can be determined.
    The equivalent line-to-neutral voltages, as a function of the sequence line-to-neutral voltages, are
    (21)
    Substitute equation (19) into equation (21):
    (22)
  Three Phase Transformer Models

## Slide 126
        The Delta-Grounded Wye Step Down Connection
    Substitute equation (16) into equation (22):
    (23)
  where (24)
    Equation (24) provides a method for computing the equivalent line-to-neutral voltages from knowledge of line-to-line voltages.
  Three Phase Transformer Models

## Slide 127
        The Delta-Grounded Wye Step Down Connection
    Equation (14) can now be substituted into equation (24).
    (25)
    where (26)
    Equation (26) defines the generalized matrix for the delta-grounded wye step-down connection.
  Three Phase Transformer Models

## Slide 128
        The Delta-Grounded Wye Step Down Connection
    The ideal secondary voltages as a function of the secondary line-to-ground voltages and the secondary line currents are:
    (27)
    where (28)
  Three Phase Transformer Models

## Slide 129
  Three Phase Transformer Models
        The Delta-Grounded Wye Step Down Connection
    Substitute equation (27) into equation (25).
  (29)
      where
  (30)

## Slide 130
        The Delta-Grounded Wye Step Down Connection
    For the generalized and matrices, we solve equation (14) for the ideal secondary voltages.
      (31)
    The line-to-line voltages as a function of the equivalent line-to-neutral voltages are:
    (32)
    where (33)
  Three Phase Transformer Models

## Slide 131
    Substituting equation (32) into equation (31) we get:
    (34)
    where (35)
    Substitute equations (27) into equation (34)
    (36)
  Three Phase Transformer Models
        The Delta-Grounded Wye Step Down Connection

## Slide 132
        The Delta-Grounded Wye Step Down Connection
    Rearrange equation (36).
    (37)
    where (38)
    Equations (29) and (37) are the generalized voltage equations for the step-down delta-grounded wye transformer.
  Three Phase Transformer Models

## Slide 133
        The Delta-Grounded Wye Step Down Connection
    For currents, the thirty degree connection specifies that the positive sequence current entering H1 terminal will lead the positive sequence currents leaving the X1 terminal by 30 degrees.
    Figure 5.0 shows the currents of the delta-grounded wye step down connection
  Three Phase Transformer Models
Figure 5.0

## Slide 134
        The Delta-Grounded Wye Step Down Connection
    Applying Kirchhoff’s Current Law (KCL):
    (38)
    (39)
    The matrix equation relating the delta primary currents to the secondary line currents is given by:
    (40)
    (41)
  Three Phase Transformer Models

## Slide 135
        The Delta-Grounded Wye Step Down Connection
    Substitute equation (41) into equation (40).
    (42)
    where (43)
    (44)
    Equation (42) provides a direct method of computing the phase line currents at node knowing the phase line currents at node .
  Three Phase Transformer Models

## Slide 136
        The Delta-Grounded Wye Step Down Connection
    The equations derived here were for the step down connection.
    The procedure for the step up connection will be the same, except the connection between the transformer windings will be different, as will be the definition of the generalized matrices.
  Three Phase Transformer Models

## Slide 137: Part 3: Three Phase Transformer Models
Three Phase Transformer Models
  General Three Phase Transformer Banks
  Generalized Matrices
  Symmetrical Components
  The Delta-Grounded Wye Step Down Connection
  The Ungrounded Wye-Delta Step Down Connection
  The Grounded Wye-Grounded Wye Connection
  The Delta-Delta Connection
  Open Wye-Open Delta
  Thevenin Equivalent Circuit

## Slide 138
        The Ungrounded Wye-Delta Step Down Connection
  Three Phase Transformer Models
    Three single-phase transformers can be connected in a wye-delta connection and the neutral of the wye can be grounded or ungrounded.
    The grounded wye is rarely used because:
      The grounded wye provides a path for the zero sequence currents for line-to-ground faults upstream from the transformer bank and can cause the transformers to be susceptible to burnouts.
      If one phase of the primary circuit is opened, the transformer bank will continue to provide a three phase service, however the remaining two transformers may be subject to overload.
    Thus, the ungrounded wye-delta connection is used to provide service to a combination of single-phase “lighting” load and a three-phase “power” load such as an induction motor.

## Slide 139
        The Ungrounded Wye-Delta Step Down Connection
  Three Phase Transformer Models
Figure 6.0

## Slide 140
    The basic ideal transformer voltage and current equations as a function of the turns ratio are:
        The Ungrounded Wye-Delta Step Down Connection
  Three Phase Transformer Models
Figure 7.0
      where (45)

## Slide 141
      (46)
      (47)
      (48)
        The Ungrounded Wye-Delta Step Down Connection
  Three Phase Transformer Models
    The basic ideal transformer voltage and current equations as a function of the turns ratio (continued):

## Slide 142
      The line-to-line voltages at node as a function of the ideal transformer voltages and the delta currents are given by:
      (50)
      (51)
  Three Phase Transformer Models
        The Ungrounded Wye-Delta Step Down Connection
      Solve equation (46) for the ideal delta transformer voltages.
        (49)

## Slide 143
        The Ungrounded Wye-Delta Step Down Connection
      Substitute equation (48) and equation (49) into equation (51).
        (52)
  where
  (53)
  Three Phase Transformer Models

## Slide 144
        The Ungrounded Wye-Delta Step Down Connection
      The line currents on the delta side of the transformer bank as a function of the wye transformer currents are given by:
    (54)
    where (55)
  Three Phase Transformer Models

## Slide 145
      Substitute equation (48) into equation (54).
      (56)
      where (57)
  Three Phase Transformer Models
        The Ungrounded Wye-Delta Step Down Connection

## Slide 146
        The Ungrounded Wye-Delta Step Down Connection
      Because the matrix is singular, it is not possible to use equation (56) to develop an equation relating the wye side line currents at node to the delta side line currents at node .
      Hence three independent equations must be written.
        Two equations are based on the KCL at the 2 vertices of the delta connection.
        The third is from the sum of the three delta currents (which will equal zero as the wye connection is ungrounded, and hence all currents on the wye side will equal zero).
  Three Phase Transformer Models

## Slide 147
        The Ungrounded Wye-Delta Step Down Connection
      Hence, the three independent equations in matrix form are given by:
(58)
      Solve equation (58) for the delta currents.
      (59)
      (60)
  Three Phase Transformer Models

## Slide 148
        The Ungrounded Wye-Delta Step Down Connection
      Equation (60) can be modified to include the phase current by setting the third column of the matrix to zero:
      (61)
      (62)
  Three Phase Transformer Models

## Slide 149
        The Ungrounded Wye-Delta Step Down Connection
      Solve equation (48) for and substitute into equation (62).
      (63)
      where (64)
      Equation (64) defines the generalized constant matrix for the ungrounded wye-delta transformer connection.
  Three Phase Transformer Models

## Slide 150
        The Ungrounded Wye-Delta Step Down Connection
      The generalized matrices and can now be developed.
      Solving equation (52) for :
      (65)
      Substitute equation (63) into equation (65):
(66)
  Three Phase Transformer Models

## Slide 151
        The Ungrounded Wye-Delta Step Down Connection
      But,
        (67)
        where (68)
        (69)
  Three Phase Transformer Models

## Slide 152
  Three Phase Transformer Models
        The Ungrounded Wye-Delta Step Down Connection
      The generalized constant matrices have been developed for computing the voltages from the load to the source.
      The reverse generalized matrices can be developed by substituting equation (52) into equation (23):
(70)

## Slide 153
  Three Phase Transformer Models
        The Ungrounded Wye-Delta Step Down Connection
where (71)
(72)

## Slide 154: Part 3: Three Phase Transformer Models
Three Phase Transformer Models
  General Three Phase Transformer Banks
  Generalized Matrices
  Symmetrical Components
  The Delta-Grounded Wye Step Down Connection
  The Ungrounded Wye-Delta Step Down Connection
  The Grounded Wye-Grounded Wye Connection
  The Delta-Delta Connection
  Open Wye-Open Delta
  Thevenin Equivalent Circuit

## Slide 155
        The Grounded Wye-Grounded Wye Connection
    The grounded wye-grounded wye connection is primarily used to supply single-phase and three-phase loads on four-wire multi-grounded systems.
  Three Phase Transformer Models
Unlike the delta-wye and wye-delta connections, there is no phase shift between the voltages and currents on the two sides of the bank.

## Slide 156
        The Grounded Wye-Grounded Wye Connection
  Three Phase Transformer Models
Figure 8.0

## Slide 157
        The Grounded Wye-Grounded Wye Connection
    With reference to Figure 8.0, the ideal transformer voltages on the secondary windings can be computed by:
    (73)
    (74)
  Three Phase Transformer Models

## Slide 158
        The Grounded Wye-Grounded Wye Connection
    The line-to-ground voltages on the primary side are related to the ideal transformer voltages by the turns ratio:
    (75)
    (76)
    Substitute equation (74) into equation (76):
    (77)
  Three Phase Transformer Models

## Slide 159
        The Grounded Wye-Grounded Wye Connection
    Equation (77) is in the generalized form with the and matrices defined by:
    (78)
    (79)
  Three Phase Transformer Models

## Slide 160
        The Grounded Wye-Grounded Wye Connection
    The primary line currents as a function of the secondary line currents is given by:
  Three Phase Transformer Models
(80)
where (81)
    The reverse equation is determined by solving equation (77) for the secondary line-to-ground voltages:
(82)

## Slide 161
  Three Phase Transformer Models
        The Grounded Wye-Grounded Wye Connection
    Constant matrices for the reverse equation are given by:
      (83)
      (84)

## Slide 162: Part 3: Three Phase Transformer Models
Three Phase Transformer Models
  General Three Phase Transformer Banks
  Generalized Matrices
  Symmetrical Components
  The Delta-Grounded Wye Step Down Connection
  The Ungrounded Wye-Delta Step Down Connection
  The Grounded Wye-Grounded Wye Connection
  The Delta-Delta Connection
  Open Wye-Open Delta
  Thevenin Equivalent Circuit

## Slide 163
        The Delta-Delta Connection
  Three Phase Transformer Models
    The delta-delta connection is primarily used on three wire systems to provide service to a three-phase load or a combination of three-phase and single-phase loads.
Figure 9.0

## Slide 164
    The basic ideal transformer voltage and current equations as a function of the turns ratio are:
    (85)
    (86)
    (87)
  Three Phase Transformer Models
        The Delta-Delta Connection

## Slide 165
    (88)
    where (89)
  Three Phase Transformer Models
        The Delta-Delta Connection
    Solve equation (88) for the source side delta currents.
(90)
    The basic ideal transformer voltage and current equations as a function of the turns ratio (continued):

## Slide 166
        The Delta-Delta Connection
    The line currents as a function of the delta currents on the source side are given by:
(91)
(92)
    Substitute equation (90) into equation (92).
(93)
  Three Phase Transformer Models

## Slide 167
        The Delta-Delta Connection
    Since is a diagonal matrix, Equation (93) can be rewritten as:
    (94)
  Three Phase Transformer Models
    The load side line currents as a function of the load side delta currents is given by:
    (95)
    (96)

## Slide 168
        The Delta-Delta Connection
    Applying equation (96), equation (94) becomes:
    (97)
    From the above equation, the load side line currents as a function of the source side line currents are given by:
    (98)
    Equation (97) and equation (98) demonstrate that the line currents on the two sides of the transformer are in phase and differ only by the turns ratio of the transformer windings.
  Three Phase Transformer Models

## Slide 169
        The Delta-Delta Connection
    The ideal delta voltages on the load side as a function of the line-to-line voltages, the delta currents, and the transformer impedances are given by:
    (99)
    where (100)
  Three Phase Transformer Models

## Slide 170
        The Delta-Delta Connection
    Substitute equation (99) into equation (86).
(101)
    Solve equation (101) for the load side line-to-line voltages.
    (102)
    The delta currents in equation (101) and equation (102) are replaced by the load side line currents .
  Three Phase Transformer Models

## Slide 171
        The Delta-Delta Connection
    Three independent equations are needed.
      Two come from applying KCL at the two vertices of the delta connected secondary.
    (103)
    (104)
      The third equation comes because the sum of the primary line-to-line voltages and, therefore, the secondary ideal transformer voltages must sum to zero. KVL around the delta windings gives:
    (105)
  Three Phase Transformer Models

## Slide 172
        The Delta-Delta Connection
    Replace the ideal delta voltages with the source side line-to-line voltages.
(106)
    As the sum of the line-to-line voltages must equal zero (KVL), and the turns ratio of the three transformers are equal, equation (106) is simplified to:
(107)
  Three Phase Transformer Models

## Slide 173
        The Delta-Delta Connection
    Equation (103), equation (104), and equation (107) can be put into the matrix form:
  (108)
    (109)
    where (110)
    (111)
  Three Phase Transformer Models

## Slide 174
        The Delta-Delta Connection
  Three Phase Transformer Models
    Solve (109) for the load side delta currents.
    (112)
    where
    (113)

## Slide 175
    Writing equation (112) in the matrix form gives:
(114)
    From equation (113) and equation (114), it can be seen that the delta currents are a function of the transformer impedances and the line currents in phases and .
  Three Phase Transformer Models
        The Delta-Delta Connection

## Slide 176
        The Delta-Delta Connection
    Equation (114) can be modified to include the line current in phase by setting the last column of the matrix to zeros.
    (115)
    The final form of equation (115) can be written as:
    (116)
    where (117)
  Three Phase Transformer Models

## Slide 177
        The Delta-Delta Connection
    The general form of the equation (117) will be used to define the generalized constant matrices for the delta-delta connection.
    Substitute equation (117) into equation (111).
    (118)
    The generalized matrices are defined in terms of the line-to-neutral voltages on the two sides of the transformer bank.
    Equation (118) is modified to be in terms of equivalent line-to-neutral voltages
(119)
  Three Phase Transformer Models

## Slide 178
        The Delta-Delta Connection
    Equation (119) is in the general form:
    (120)
    where (121)
    (122)
  Three Phase Transformer Models

## Slide 179
    Equation (97) gives the generalized equation for currents.
    (123)
where (124)
  Three Phase Transformer Models
        The Delta-Delta Connection

## Slide 180
    The reverse generalized equation can be derived by modifying Equation (102) in terms of equivalent line-to-neutral voltages.
(125)
      (126)
where (127)
(128)
  Three Phase Transformer Models
        The Delta-Delta Connection

## Slide 181: Part 3: Three Phase Transformer Models
Three Phase Transformer Models
  General Three Phase Transformer Banks
  Generalized Matrices
  Symmetrical Components
  The Delta-Grounded Wye Step Down Connection
  The Ungrounded Wye-Delta Step Down Connection
  The Grounded Wye-Grounded Wye Connection
  The Delta-Delta Connection
  Open Wye-Open Delta
  Thevenin Equivalent Circuit

## Slide 182
        Open Wye-Open Delta
    A distribution feeder commonly serves a combination of both single phase and three phase loads.
    This combination can be served with an ungrounded wye-delta connection as previously described.
    When the three phase load is small compared to the single phase load, the “open wye-open delta” combination is commonly used.
    The advantage of the open wye-open delta connection is that it requires only two transformers, but can provide three-phase line-to-line voltages to the combination load.
  Three Phase Transformer Models

## Slide 183
  Three Phase Transformer Models
        Open Wye-Open Delta
Figure 10.0
    Figure 10.0 shows the open wye-open delta connection and the primary and secondary positive sequence voltage phasors.

## Slide 184
        Open Wye-Open Delta
    With reference to Figure 10.0, the basic ideal transformer voltages as a function of the “turns ratio” are:
    (129)
    (130)
  Three Phase Transformer Models

## Slide 185
        Open Wye-Open Delta
    The currents as a function of the turns ratio are given by:
  Three Phase Transformer Models
(131)
    Equation (131) can be expressed in matrix form by:
    (132)
    (133)

## Slide 186
  Three Phase Transformer Models
        Open Wye-Open Delta
    The ideal voltages on the delta windings can be determined by:
    Apply equation (129) to equation (134).
(134)
(135)

## Slide 187
        Open Wye-Open Delta
    Equation (135) can be put into three-phase matrix form as:
    (136)
    (137)
    The secondary line-to-line voltages in equation (137) can be replaced by the equivalent line-to-neutral secondary voltages.
    (138)
  Three Phase Transformer Models

## Slide 188
        Open Wye-Open Delta
    The generalized matrix equation becomes:
    (139)
    where (140)
    (142)
  Three Phase Transformer Models

## Slide 189
  Three Phase Transformer Models
        Open Wye-Open Delta
    The source side line currents as a function of the load side line currents are given by:
(143)
(144)
where (145)

## Slide 190
  Three Phase Transformer Models
        Open Wye-Open Delta
    For deriving the reverse equation, relating the secondary equivalent line-to-neutral voltages as a function of the source side line-to-ground voltages and line currents, we first obtain the two line-to-line secondary voltages.
(146)

## Slide 191
        Open Wye-Open Delta
    The third line-to-line voltage () must be equal to the negative sum of the other two line-to-line voltages(KVL). In the matrix form, the desired equation is:
    (147)
    (148)
  Three Phase Transformer Models

## Slide 192
    The generalized reverse equation is given by:
    (150)
  Three Phase Transformer Models
        Open Wye-Open Delta
    The equivalent secondary line-to-neutral voltages are given by:
and
(149)

## Slide 193
    where
    (151)
    (152)
  Three Phase Transformer Models
        Open Wye-Open Delta

## Slide 194
        Open Wye-Open Delta
    The equations derived on the previous slide are for an open-wye-open delta connection on phases A and B on the primary.
    The same methodology can be adopted to derive the equations when the transformers are on phases B and C or A and C on the primary.
    The terms “leading” and “lagging” connection are also associated with the open wye-open delta connection.
  Three Phase Transformer Models

## Slide 195
        Open Wye-Open Delta
    When the “lighting” transformer is connected across the leading of the two phases, it is known as “leading” connection.
      For example when connected from phase A to ground, the connection would be known as a leading connection.
    When the “lighting” transformer is connected across the lagging of the two phases, it is known as a “lagging” connection.
      For example, when the connection is from the ground to phase A, it is known as a lagging connection
  Three Phase Transformer Models

## Slide 196: Part 3: Three Phase Transformer Models
Three Phase Transformer Models
  General Three Phase Transformer Banks
  Generalized Matrices
  Symmetrical Components
  The Delta-Grounded Wye Step Down Connection
  The Ungrounded Wye-Delta Step Down Connection
  The Grounded Wye-Grounded Wye Connection
  The Delta-Delta Connection
  Open Wye-Open Delta
  Thevenin Equivalent Circuit

## Slide 197
        Thevenin Equivalent Circuit
    The Thevenin equivalent circuit referenced to the secondary terminals of the transformer must take into account the equivalent impedance between the primary terminals of the transformer and the feeder source.
    Figure 11.0 is a general circuit showing the feeder source down to the secondary bus.
      Figure 11.0
  Three Phase Transformer Models

## Slide 198
        Thevenin Equivalent Circuit
    The Thevenin equivalent is obtained by “referring” the source voltage and the source impedance to the secondary side of the transformer.
  Three Phase Transformer Models
    The desired Thevenin equivalent circuit at the transformer secondary node is shown in Figure 12.0.
    Figure 12.0

## Slide 199
        Thevenin Equivalent Circuit
    In Figure 11.0, the primary transformer equivalent line-to-neutral voltages as a function of the source voltage and the equivalent high side impedance is given by:
    (153)
    But
    Therefore,
    (154)
  Three Phase Transformer Models

## Slide 200
        Thevenin Equivalent Circuit
    The general reverse equation gives the secondary line-to-neutral voltages as a function of the primary line-to-neutral voltages:
    (155)
    Substitute equation (154) into equation (155).
(156)
  Three Phase Transformer Models

## Slide 201
        Thevenin Equivalent Circuit
    With reference to equation (156), the Thevenin equivalent voltages and impedances can be defined as:
(157)
    (158)
    The definition of the Thevenin equivalent voltages and impedances as given in equation (157) and equation (158) are general and can be used for all transformer connections.
  Three Phase Transformer Models

## Slide 202: Part 4: Center –Tapped Transformers and Secondaries
Center –Tapped Transformers and Secondaries
  Center-Tapped Single-Phase Transformer
    Matrix Equations
    Center-Tapped Transformer Serving Loads through a Triplex Secondary
  Underground Wye-Delta Transformer Bank with a Center Tapped Transformer
  Leading Open Wye-Open Delta Transformer Connection
  Lagging Open Wye-Open Delta Connection
  Four Wire Secondary

## Slide 203
    The standard method of providing three-wire service is from a center-tapped single-phase transformer.
    In this type of connection there are two 120 volt circuits and one 240-volt circuit.
    There are two types of center tapped transformers.
Center-Tapped Single-Phase Transformer

## Slide 204
    The first is as shown in Figure 13.0.
    Figure 13.0
    Here the secondary consists of one winding that is center tapped. The secondary voltage of this transformer will be specified as 240/120 volts.
    The 240/120 volts secondary rating specifies that the full winding voltage is 240 volts with the center tap providing two 120 volt circuits.
Center-Tapped Single-Phase Transformer

## Slide 205
    A second type is as shown in Figure 14.0.
        Figure 14.0
    Here the transformer consists of a three winding transformer with the two secondary windings connected in series.
    The secondary of this transformer is specified in 120/240 volts.
Center-Tapped Single-Phase Transformer

## Slide 206
    The model of the center-tapped transformer of Figure 13.0 and 14.0 is shown in Figure 15.0.
    Figure 15.0
    It can either represent the model of the center tapped transformer of Figure 13.0 or the two secondary windings connected in series of Figure 14.0.
Center-Tapped Single-Phase Transformer

## Slide 207
    The first step to developing the model is to determine the impedances , , .
    The values of and in per-unit based upon transformer ratings are given in Turan Gonen’s Electric Power Distribution System Engineering.
    Empirical equations are commonly used to convert the transformer impedance to the winding impendences.
Center-Tapped Single-Phase Transformer

## Slide 208
    For an interlaced designed, these equations are given by:
(159)
    For a non-interlaced designed, these equations are given by:
    (160)
Center-Tapped Single-Phase Transformer

## Slide 209: Part 4: Center –Tapped Transformers and Secondaries
Center –Tapped Transformers and Secondaries
  Center-Tapped Single-Phase Transformer
    Matrix Equations
    Center-Tapped Transformer Serving Loads through a Triplex Secondary
  Underground Wye-Delta Transformer Bank with a Center Tapped Transformer
  Leading Open Wye-Open Delta Transformer Connection
  Lagging Open Wye-Open Delta Connection
  Four Wire Secondary

## Slide 210
        Matrix Equations
      Referring to Figure 13.0, the ideal secondary voltages of the transformer are:
Center-Tapped Single-Phase Transformer
(161)
(162)

## Slide 211
        Matrix Equations
      The ideal primary voltage as a function of the secondary ideal voltages is:
        where (163)
Center-Tapped Single-Phase Transformer
(162)

## Slide 212
Center-Tapped Single-Phase Transformer
        Matrix Equations
      The primary transformer current as a function of the secondary winding currents is given in equation (164).
      The negative sign is due to the selected direction of the current
(164)

## Slide 213
Center-Tapped Single-Phase Transformer
        Matrix Equations
      Substitute equations (161) into equations (162).
(165)
      The source voltage as a function of the ideal primary voltage is:
(166)

## Slide 214
        Matrix Equations
      Substitute equations (165) into equations (166):
          (167)
      Substitute equations (164) into equations (167):
Center-Tapped Single-Phase Transformer
(168)

## Slide 215
        Matrix Equations
      Equation (168) is of the form:
(169)
      where
    (170)
Center-Tapped Single-Phase Transformer
(171)

## Slide 216
        Matrix Equations
    Equation (164) is of the form:
where (172)
    Equation (169) is used to compute the primary source voltage when the secondary terminal voltages and the secondary currents are known.
Center-Tapped Single-Phase Transformer

## Slide 217
Center-Tapped Single-Phase Transformer
        Matrix Equations
    The reverse equations for determining the secondary terminal voltage when the primary source voltage and secondary currents are known are obtained by solving equation (169) for the secondary terminal voltages.
    (173)

## Slide 218
Center-Tapped Single-Phase Transformer
        Matrix Equations
where
    (174)

## Slide 219: Part 4: Center –Tapped Transformers and Secondaries
Center –Tapped Transformers and Secondaries
  Center-Tapped Single-Phase Transformer
    Matrix Equations
    Center-Tapped Transformer Serving Loads through a Triplex Secondary
  Underground Wye-Delta Transformer Bank with a Center Tapped Transformer
  Leading Open Wye-Open Delta Transformer Connection
  Lagging Open Wye-Open Delta Connection
  Four Wire Secondary

## Slide 220
  Center-Tapped Transformer Serving Loads through a Triplex Secondary
    Figure 16.0 shows a center-tapped transformer serving a load through a triplex secondary.
        Figure 16.0
Center-Tapped Single-Phase Transformer

## Slide 221
    The impedance matrix of the triplex secondary is determined using Carson’s equation.
    Apply Carson’s equations:
Center-Tapped Single-Phase Transformer
  Center-Tapped Transformer Serving Loads through a Triplex Secondary
    A triplex secondary consisting of two insulated conductors and one un-insulated neutral conductor is as shown in Figure 17.0.
Figure 17.0
(175)

## Slide 222
  Center-Tapped Transformer Serving Loads through a Triplex Secondary
    The secondary voltage equation in the matrix form is:
(176)
    When the neutral is grounded at the transformer and the load then:
(177)
    This leads to the Kron reduction equation in partitioned form:
      (178)
Center-Tapped Single-Phase Transformer

## Slide 223
    Solving equation (178) for the neutral current:
  define (180)
Center-Tapped Single-Phase Transformer
  Center-Tapped Transformer Serving Loads through a Triplex Secondary
(179)

## Slide 224
  Center-Tapped Transformer Serving Loads through a Triplex Secondary
    Substituting equation (178) into equation (180) and solving for the voltage drops we get:
(181)
define
(182)
Center-Tapped Single-Phase Transformer

## Slide 225
  Center-Tapped Transformer Serving Loads through a Triplex Secondary
    For a secondary of length :
  (183)
    Referring to Figure 16.0, the secondary output voltages of the transformer are given by:
    (184)
    The transformer primary voltage is given by equation (172).
Center-Tapped Single-Phase Transformer

## Slide 226
  Center-Tapped Transformer Serving Loads through a Triplex Secondary
    Substituting equation (184) into equation (172):
(185)
where
Center-Tapped Single-Phase Transformer

## Slide 227
Center-Tapped Single-Phase Transformer
  Center-Tapped Transformer Serving Loads through a Triplex Secondary
    Since there are no shunt elements in the secondary, the primary current as a function of the secondary currents is still given by equation (164).
    Equation (185) can be used to solve for the load voltages when the primary source voltages and the secondary currents are known.
    where (186)

## Slide 228
Center-Tapped Single-Phase Transformer
  Center-Tapped Transformer Serving Loads through a Triplex Secondary
    In the matrix form, equation (186) can be given by:
(187)

## Slide 229: Part 4: Center –Tapped Transformers and Secondaries
Center –Tapped Transformers and Secondaries
  Center-Tapped Single-Phase Transformer
    Matrix Equations
    Center-Tapped Transformer Serving Loads through a Triplex Secondary
  Underground Wye-Delta Transformer Bank with a Center Tapped Transformer
  Leading Open Wye-Open Delta Transformer Connection
  Lagging Open Wye-Open Delta Connection
  Four Wire Secondary

## Slide 230
  Underground Wye-Delta Transformer Bank with a Center Tapped Transformer
    Ungrounded wye-delta transformer connection is used for providing service to a combination of three-phase and single-phase loads.
    In order to provide three-wire service for single-phase loads, one of the transformers is a center tap transformer.
    This transformer is called the “lighting” transformer and the other two transformers are called the “power” transformers.
Center-Tapped Single-Phase Transformer

## Slide 231
Center-Tapped Single-Phase Transformer
  Underground Wye-Delta Transformer Bank with a Center Tapped Transformer
    Figure 18.0 : Ungrounded wye-delta with center-tapped transformer

## Slide 232
  Underground Wye-Delta Transformer Bank with a Center Tapped Transformer
      Backward Sweep Equations
    In order to compute the source side voltages and currents from the secondary side voltages and currents, from Figure 18.0, define the secondary terminal voltages as:
(188)
Center-Tapped Single-Phase Transformer

## Slide 233
  Underground Wye-Delta Transformer Bank with a Center Tapped Transformer
    The secondary line currents and the currents flowing inside the delta are defined as:
      (189) (190)
    The transformer ratio is defined as:
(191)
Center-Tapped Single-Phase Transformer

## Slide 234
  Underground Wye-Delta Transformer Bank with a Center Tapped Transformer
    The matrix equation relating the primary ideal transformer voltages to the secondary ideal voltages is:
    (192)
    The primary terminal voltages are given by:
(193)
Center-Tapped Single-Phase Transformer

## Slide 235
  Underground Wye-Delta Transformer Bank with a Center Tapped Transformer
    Substitute equation (192) into equation (193).
(194)
    The primary line currents as a function of the secondary delta currents are given by:
(195)
Center-Tapped Single-Phase Transformer

## Slide 236
  Underground Wye-Delta Transformer Bank with a Center Tapped Transformer
    Substitute equation (195) into equation (194):
(196)
    The secondary ideal transformer voltages are given by:
(197)
Center-Tapped Single-Phase Transformer

## Slide 237
    Substitute equation (190) into equation (196):
(198)
Center-Tapped Single-Phase Transformer
  Underground Wye-Delta Transformer Bank with a Center Tapped Transformer

## Slide 238: Part 4: Center –Tapped Transformers and Secondaries
Center –Tapped Transformers and Secondaries
  Center-Tapped Single-Phase Transformer
    Matrix Equations
    Center-Tapped Transformer Serving Loads through a Triplex Secondary
  Underground Wye-Delta Transformer Bank with a Center Tapped Transformer
  Leading Open Wye-Open Delta Transformer Connection
  Lagging Open Wye-Open Delta Connection
  Four Wire Secondary

## Slide 239
  Leading Open Wye-Open Delta Transformer Connection
The leading open wye-open delta connection consists of one lighting and one power transformer used to serve a combination of single-phase and three-phase loads.
The leading open wye-open delta connection and the no-load voltage phasors for this connection are as shown in Figure 19.0 and Figure 20.0.
Center-Tapped Single-Phase Transformer

## Slide 240
  Leading Open Wye-Open Delta Transformer Connection
Center-Tapped Single-Phase Transformer
Figure 19.0

## Slide 241
Unlike the closed delta, there is a direct relationship between the secondary transformer currents and the line currents.
Hence, applying KCL in Figure 19.0, the currents flowing in the open delta as a function of the line currents are given by:
Center-Tapped Single-Phase Transformer
  Leading Open Wye-Open Delta Transformer Connection
Figure 20.0
(200)

## Slide 242
The primary and secondary ideal transformer voltages going from the secondary to the primary are related by:
(201)
Center-Tapped Single-Phase Transformer
  Leading Open Wye-Open Delta Transformer Connection

## Slide 243
Center-Tapped Single-Phase Transformer
  Leading Open Wye-Open Delta Transformer Connection
The primary and transformer secondary currents are related by:
(202)

## Slide 244
  Leading Open Wye-Open Delta Transformer Connection
Going from the primary ideal transformer voltages to the secondary ideal voltages (forward sweep), the voltages are related by:
(203)
Center-Tapped Single-Phase Transformer

## Slide 245
For this open wye-open delta connection, the transformer impedance matrices are defined as:
(204)
Center-Tapped Single-Phase Transformer
  Leading Open Wye-Open Delta Transformer Connection

## Slide 246
Equation (199):
Center-Tapped Single-Phase Transformer
  Leading Open Wye-Open Delta Transformer Connection
(199)
Equation (199) is now used to determine the forward and backward matrices.

## Slide 247: Part 4: Center –Tapped Transformers and Secondaries
Center –Tapped Transformers and Secondaries
  Center-Tapped Single-Phase Transformer
    Matrix Equations
    Center-Tapped Transformer Serving Loads through a Triplex Secondary
  Underground Wye-Delta Transformer Bank with a Center Tapped Transformer
  Leading Open Wye-Open Delta Transformer Connection
  Lagging Open Wye-Open Delta Connection
  Four Wire Secondary

## Slide 248
  Lagging Open Wye-Open Delta Connection
In the lagging open wye-open delta connection, the transformer serving the single phase load is connected across the voltage that lags the power transformer by 120 degrees.
Center-Tapped Single-Phase Transformer
A number of connections can be used to achieve the lagging open wye-open delta connection, Figure 21.0 shows the connection that will be used here.

## Slide 249
  Lagging Open Wye-Open Delta Connection
Center-Tapped Single-Phase Transformer
Figure 21.0

## Slide 250
In Figure 21.0, the lighting transformer is connected to phase C and the power transformer is connected to phase A.
The no-load phasor voltage phasor diagrams for this connection are shown in Figure 22.0.
                Figure 22.0
Center-Tapped Single-Phase Transformer
  Lagging Open Wye-Open Delta Connection

## Slide 251
  Lagging Open Wye-Open Delta Connection
With this connection, the phasing of the secondary will remain the same as the leading connection. Hence the definition of the matrix will remain the same as equation (200).
The primary and the secondary ideal transformer voltages going from the secondary to the primary are related by:
(205)
Center-Tapped Single-Phase Transformer

## Slide 252
  Lagging Open Wye-Open Delta Connection
The primary and transformer secondary currents are related by:
(206)
Center-Tapped Single-Phase Transformer

## Slide 253
Going from the primary ideal transformer voltages to the secondary ideal voltages (forward sweep) the voltages are related by:
(207)
Center-Tapped Single-Phase Transformer
  Lagging Open Wye-Open Delta Connection

## Slide 254
For this open wye-open delta connection, the transformer impedance matrix are defined as:
(208)
    Equation (199) is again used to determine the forward and backward matrices.
Center-Tapped Single-Phase Transformer
  Lagging Open Wye-Open Delta Connection

## Slide 255: Part 4: Center –Tapped Transformers and Secondaries
Center –Tapped Transformers and Secondaries
  Center-Tapped Single-Phase Transformer
    Matrix Equations
    Center-Tapped Transformer Serving Loads through a Triplex Secondary
  Underground Wye-Delta Transformer Bank with a Center Tapped Transformer
  Leading Open Wye-Open Delta Transformer Connection
  Lagging Open Wye-Open Delta Connection
  Four Wire Secondary

## Slide 256
  Four Wire Secondary
Typically a combination of single-phase and three-phase loads will be connected to transformer through a length of open four-wire secondary or a quadraplex cable secondary.
Center-Tapped Single-Phase Transformer
Figure 23.0

## Slide 257
The self and mutual impedances of the four-wire secondary are calculated using Carson’s equations and Kron reduction, thus giving a 3X3 impedance matrix.
The voltage drops on the three line conductors are:
(209)
Center-Tapped Single-Phase Transformer
  Four Wire Secondary

## Slide 258
      Write the KVL around the three “window” loops and the outside loop in Figure 21.0.
(210)
Center-Tapped Single-Phase Transformer
  Four Wire Secondary

## Slide 259
Substitute Equation (109) into Equation (210).
(211)
Center-Tapped Single-Phase Transformer
  Four Wire Secondary

## Slide 260
Center-Tapped Single-Phase Transformer
  Four Wire Secondary
Equation (211) is in the form of:
where
(212)

## Slide 261
  Four Wire Secondary
Since there are no shunt devices between the transformer and the loads, the currents leaving the transformer are equal to the line currents serving the loads. Thus
(213)
  The matrices for the forward sweep are:
(214)
Center-Tapped Single-Phase Transformer

## Slide 262: Part 4: IEEE Test Systems
  IEEE 4 Bus System
  IEEE 13 Bus System
  IEEE 37 Bus System
  IEEE 8500 Node System

## Slide 263
  IEEE Test Systems
  IEEE 4 Bus System

## Slide 264
  IEEE Test Systems
  IEEE 13 Bus System

## Slide 265
  IEEE Test Systems
  IEEE 37 Bus System

## Slide 266
  IEEE Test Systems
  IEEE 8500 Node System

## Slide 267: Module 2 Concluding Comments
1
2
3
4