## Slide 1: Substation and Distribution Automation Module 2
Overhead Lines Underground lines

## Slide 2: Module 1 Overview
Part 1: Overhead Lines
Part 2: Underground lines
Part 3: Three Phase Transformer Models
Part 4: Center –Tapped Transformers and Secondaries
Part 5: IEEE Test Systems

## Slide 3: Part 1: Overhead Lines
Series impedance of Overhead Lines
  Transposed Three-phase Lines
  Untransposed Distribution Lines
  Carson’s Equations
  Modified Carson’s Equations
  Primitive Impedance Matrix for Overhead Lines
  Phase Impedance Matrix for Overhead Lines
  Sequence Impedances
  Parallel Overhead Distribution Lines
Shunt Admittance of Overhead Parallel Lines
General Voltage Drop Equation (examples from Kevin)

## Slide 4
Series impedance of Overhead Lines
Critical step before the analysis of the distribution feeder can begin.
Resistance component of the conductors is typically taken from a look-up table (can be found in Appendix A of the text book)
The reactance comes from the inductive reactance (self and mutual) of the conductors. The inductive reactance is due to the magnetic field surrounding the conductors.

## Slide 5
Series impedance of Overhead Lines
Figure 1.0 shows magnetic flux lines created by currents flowing through conductors to (current is flowing outwards here)
Figure 1.0

## Slide 6
It is further assumed the sum of the currents will be zero. That is
(1)
The total flux linking the conductor is given by:
W-T/m (2)
where: Distance between conductor and conductor (ft.)
= Geometric Mean Radius of conductor (ft.)
Series impedance of Overhead Lines (Contd…)

## Slide 7
Series impedance of Overhead Lines (Contd…)
Inductance is given by the flux linkage divided by the current.
Thus, the inductance of the conductor consists of the “self inductance” of the conductor and the “mutual inductance” between conductor and the other conductors.
Self Inductance: H/m (3)
Mutual Inductance: H/m (4)

## Slide 8: Part 1: Overhead Lines
Series impedance of Overhead Lines
  Transposed Three-phase Lines
  Untransposed Distribution Lines
  Carson’s Equations
  Modified Carson’s Equations
  Primitive Impedance Matrix for Overhead Lines
  Phase Impedance Matrix for Overhead Lines
  Sequence Impedances
  Parallel Overhead Distribution Lines
Shunt Admittance of Overhead Parallel Lines
General Voltage Drop Equation

## Slide 9
Series impedance of Overhead Lines
Transposed Three-phase Lines
Usual assumptions made for High-Voltage Transmission lines:
    Transposed – Each phase occupies the same physical position on the structure for one-third of the length of the line.
    Balanced Loading – All phases are equally loaded.
Hence “self” and “mutual” inductance terms can be combined into one “phase” inductance.
The series impedance per phase of a transposed three-phase line consisting of one conductor per phase is given by:
Series Impedance: Ω/mile (5)

## Slide 10: Part 1: Overhead Lines
Series impedance of Overhead Lines
  Transposed Three-phase Lines
  Untransposed Distribution Lines
  Carson’s Equations
  Modified Carson’s Equations
  Primitive Impedance Matrix for Overhead Lines
  Phase Impedance Matrix for Overhead Lines
  Sequence Impedances
  Parallel Overhead Distribution Lines
Shunt Admittance of Overhead Parallel Lines
General Voltage Drop Equation

## Slide 11
Untransposed Distribution Lines
Distribution Systems consist of single-phase, two-phase and untransposed three-phase lines serving unbalanced loads.
Hence it is necessary to retain the identity of the self and mutual impedance terms of the conductors in addition to taking into account the ground return path for the unbalanced currents.
The resistance of the conductors is taken directly from the table of conductor data.
Series impedance of Overhead Lines (Contd…)

## Slide 12
Untransposed Distribution Lines
Equations (3) and (4) are used to calculate self and mutual reactances of the conductors.
  Recall:
Series impedance of Overhead Lines (Contd…)
H/m (3)
H/m (4)

## Slide 13
Untransposed Distribution Lines
Assumptions
  Inductive reactance will be at a frequency of 60 Hz.
  Length of the conductor is one mile.
The self and mutual impedances are given by
Series impedance of Overhead Lines (Contd…)
Ω/mile (6)
Ω/mile (7)

## Slide 14
Two Conductors with Dirt Return
Figure 2.0

## Slide 15
Two Conductors with Dirt Return
Voltage between conductor and ground (using Kirchhoff’s Voltage Law):
(8)
Collect terms and use:
(from KVL) (9)
to get:
(10)
where:
(11)
(12)

## Slide 16
Primitive Circuit Impedances
Series impedance of Overhead Lines (Contd…)
Figure 3.0

## Slide 17
Primitive Circuit Impedances
Series impedance of Overhead Lines (Contd…)
(13)
(14)
Substitute the self and mutual impedance equations:
Ω/mile (6)
Ω/mile (7)
into our “hat” impedances (eq’s 11 and 12)
to get the primitive self and mutual impedances:

## Slide 18: Part 1: Overhead Lines
Series impedance of Overhead Lines
  Transposed Three-phase Lines
  Untransposed Distribution Lines
  Carson’s Equations
  Modified Carson’s Equations
  Primitive Impedance Matrix for Overhead Lines
  Phase Impedance Matrix for Overhead Lines
  Sequence Impedances
  Parallel Overhead Distribution Lines
Shunt Admittance of Overhead Parallel Lines
General Voltage Drop Equation

## Slide 19
Carson’s Equations
Because distribution is inherently unbalanced, the most accurate analysis should not make any assumptions regarding :
  the spacing between conductors
  conductor sizes
  transposition
Carson assumes the earth is an infinite, uniform solid, with a flat uniform upper surface and a constant resistivity.
Any “end effects” introduced at the neutral grounding points are not large at power frequencies, and there, are neglected.
Series impedance of Overhead Lines (Contd…)

## Slide 20
Carson made use of conductor images; that is, every conductor at a given distance above ground has an image conductor at the same distance below-ground.
Series impedance of Overhead Lines (Contd…)
Carson’s Equations
Ω/mile (15)
Ω/mile (16)
Self Impedance:
Mutual Impedance:
Figure 4.0

## Slide 21
Series impedance of Overhead Lines (Contd…)
Carson’s Equations
Variable Definitions
system angular frequency in radians per second
Ω/mile
radius of conductor in feet
system frequency in Hertz
resistivity of earth in Ω-meters
distance between conductors and in feet (see Figure)
distance between conductors and image in feet (see Figure)
angle between a pair of lines drawn from conductor to its own image and to the image of conductor

## Slide 22
Series impedance of Overhead Lines (Contd…)
Carson’s Equations
Variable Definitions (Contd…)
Ω/mile (17)
(18)
(19)
(20)

## Slide 23: Part 1: Overhead Lines
Series impedance of Overhead Lines
  Transposed Three-phase Lines
  Untransposed Distribution Lines
  Carson’s Equations
  Modified Carson’s Equations
  Primitive Impedance Matrix for Overhead Lines
  Phase Impedance Matrix for Overhead Lines
  Sequence Impedances
  Parallel Overhead Distribution Lines
Shunt Admittance of Overhead Parallel Lines
General Voltage Drop Equation

## Slide 24
Modified Carson’s Equations: Derivation
Approximations:
(21)
(22)
Substitute Eq’n 20 (the value of ) into (22) and simplify:
(23)
(24)
(25)
Now simplify the Carson’s Eq’s (substituting in the first):

## Slide 25
Modified Carson’s Equations: Derivation
Substitute expressions for and
(26)
(27)
Now substitute our expression for and values and :
(28)
(29)

## Slide 26
Modified Carson’s Equations
Series impedance of Overhead Lines (Contd…)
Assume:
frequency = 60 Hertz
earth resistivity = 1000 Ohm-meters
Hence the modified Carson’s equations are:
Ω/mile (30)
Ω/mile (31)

## Slide 27
Comparing Equations
Series impedance of Overhead Lines (Contd…)
(13)
(14)
(30)
(31)
Modified Carson’s:
Primitive Impedance:

## Slide 28: Part 1: Overhead Lines
Series impedance of Overhead Lines
  Transposed Three-phase Lines
  Untransposed Distribution Lines
  Carson’s Equations
  Modified Carson’s Equations
  Primitive Impedance Matrix for Overhead Lines
  Phase Impedance Matrix for Overhead Lines
  Sequence Impedances
  Parallel Overhead Distribution Lines
Shunt Admittance of Overhead Parallel Lines
General Voltage Drop Equation

## Slide 29
(32)
Primitive Impedance Matrix for Overhead Lines
The Modified Carson’s Equations (30 & 31) are used to compute the elements of the “primitive impedance matrix”.
The primitive impedance matrix for a three-phase line consisting of neutrals will be of the form:
Series impedance of Overhead Lines (Contd…)

## Slide 30
Primitive Impedance Matrix for Overhead Lines
In partitioned form, Equation (32) becomes:
Series impedance of Overhead Lines (Contd…)
(33)

## Slide 31: Part 1: Overhead Lines
Series impedance of Overhead Lines
  Transposed Three-phase Lines
  Untransposed Distribution Lines
  Carson’s Equations
  Modified Carson’s Equations
  Primitive Impedance Matrix for Overhead Lines
  Phase Impedance Matrix for Overhead Lines
  Sequence Impedances
  Parallel Overhead Distribution Lines
Shunt Admittance of Overhead Parallel Lines
General Voltage Drop Equation

## Slide 32
Phase Impedance Matrix for Overhead Lines
Series impedance of Overhead Lines (Contd…)
For most applications, the primitive impedance matrix needs to be reduced to a 3X3 “phase frame” matrix consisting of the self and mutual equivalent impedances for the three phases. Figure 5.0 shows a four-wire grounded neutral line segment
Figure 5.0

## Slide 33
Phase Impedance Matrix for Overhead Lines (Contd…)
Series impedance of Overhead Lines (Contd…)
= + (34)
Figure 5.0

## Slide 34
Phase Impedance Matrix for Overhead Lines
One standard method of reduction is the “Kron” reduction. The Kron reduction method applies KVL to the circuit.
Series impedance of Overhead Lines (Contd…)
In partitioned form, (34) becomes:
(35)
Because the neutral is grounded, voltages and equal 0.
Thus
(36)
(37)

## Slide 35
Phase Impedance Matrix for Overhead Lines
Series impedance of Overhead Lines (Contd…)
Solve (37) for :
(38)
Substitute (38) into expression (36):
(39)
where
(40)

## Slide 36
After having applied the Kron reduction technique, the final phase impedance matrix becomes:
(41)
Series impedance of Overhead Lines (Contd…)
Phase Impedance Matrix for Overhead Lines
Ω/mile

## Slide 37
Phase Impedance Matrix for Overhead Lines
The phase impedance matrix for a three-wire delta line is determined by the application of Carson’s equations without the Kron reduction step.
The phase impedance matrix can be used to accurately determine the voltage drops on the feeder line segments once the currents have been determined.
Since no approximations (transpositions for example) have been made regarding the spacing between conductors, the effect of the mutual coupling between the phases is accurately taken into account.
Series impedance of Overhead Lines (Contd…)

## Slide 38
Phase Impedance Matrix for Overhead Lines
The application of the Modified Carson’s equations and the phase frame matrix lead to the most accurate model of a line segment as shown in Figure 6.0.
Series impedance of Overhead Lines (Contd…)
Figure 6.0

## Slide 39
Phase Impedance Matrix for Overhead Lines
Series impedance of Overhead Lines (Contd…)
length

## Slide 40: Part 1: Overhead Lines
Series impedance of Overhead Lines
  Transposed Three-phase Lines
  Untransposed Distribution Lines
  Carson’s Equations
  Modified Carson’s Equations
  Primitive Impedance Matrix for Overhead Lines
  Phase Impedance Matrix for Overhead Lines
  Sequence Impedances
  Parallel Overhead Distribution Lines
Shunt Admittance of Overhead Parallel Lines
General Voltage Drop Equation

## Slide 41
Sequence Impedances
Many times the analysis of a feeder will use only the positive and zero sequence impedances for the line segments. There are 2 methods for obtaining these impedances.
The first method uses the Modified Carson’s Equations and the Kron reduction to obtain the phase impedance matrix.
The definition of line-to-ground phase voltages as a function of the line-to-ground sequence voltages is given by
Series impedance of Overhead Lines (Contd…)
(42)
where

## Slide 42
Sequence Impedances
In condensed form Equation (42) becomes:
(43)
  where
(44)
The phase line currents can be defined in the same manner.
(45)
Series impedance of Overhead Lines (Contd…)

## Slide 43
Sequence Impedances
Equation (43) can be used to solve for the sequence line-to-ground voltages as a function of the phase line-to-ground voltages.
(46)
  where:
(47)
Series impedance of Overhead Lines (Contd…)

## Slide 44
The voltage equation in matrix form for the line segment:
can be transformed to the sequence domain by multiplying both sides by and also substituting in the definition of the phase currents as given by Equation (43).
(48)
where:
(49)
Series impedance of Overhead Lines (Contd…)
Sequence Impedances

## Slide 45
Sequence Impedances
  Equation (48) in expanded form is given by
Series impedance of Overhead Lines (Contd…)
Equation (49) is the defining equation for converting phase impedances to sequence impedances. In equation (49), the diagonal terms of the matrix are the sequence impedances of the line such that:
(50)

## Slide 46
Sequence Impedances
<Kevin’s example of sequential components not being equal to phase components. In any commercial tool, often diagonal components are ignored>
Series impedance of Overhead Lines (Contd…)

## Slide 47
Sequence Impedances
The off-diagonal terms of Equation (49) represent the mutual coupling between sequences.
If the lines were transposed, these off-diagonal terms would be zero. This will generally be true for off-diagonal terms.
For transposed lines, the phase impedance matrix is modified so the three diagonal terms are equal, and all of the off-diagonal terms are equal.
Usually, the procedure is to set the three diagonal terms of the phase impedance matrix equal to the average of the diagonal terms of Equation (41) and the off-diagonal terms equal to the average of the off-diagonal terms of Equation (41).
Series impedance of Overhead Lines (Contd…)

## Slide 48
Sequence Impedances for transposed lines
Series impedance of Overhead Lines (Contd…)
Ω/mile (51)
Ω/mile (52)
Ω/mile (52)
Self and Mutual Impedance defined as:
Phase Impedance matrix:

## Slide 49
Sequence Impedances for transposed lines
Series impedance of Overhead Lines (Contd…)
Ω/mile (54)
Ω/mile (55)
Determine Sequence Impedances:

## Slide 50
Sequence Impedances
A second method that is commonly used to determine the sequence impedances directly is to employ the concept of Geometric Mean Distances (GMD).
Series impedance of Overhead Lines (Contd…)
GMD between phases:
(56)
GMD between phases and neutral:
(57)

## Slide 51
Sequence Impedances
Series impedance of Overhead Lines (Contd…)
The above GMD’s are used in the Modified Carson Equations, resulting in:
Ω/mile (58)
Ω/mile (59)
Ω/mile (60)
Ω/mile (61)

## Slide 52: Part 1: Overhead Lines
Series impedance of Overhead Lines
  Transposed Three-phase Lines
  Untransposed Distribution Lines
  Carson’s Equations
  Modified Carson’s Equations
  Primitive Impedance Matrix for Overhead Lines
  Phase Impedance Matrix for Overhead Lines
  Sequence Impedances
  Parallel Overhead Distribution Lines
Shunt Admittance of Overhead Parallel Lines
General Voltage Drop Equation

## Slide 53
    Parallel Overhead Lines
    It is fairly common in a distribution system to find instances where two distribution lines are “physically” parallel.
    The phase impedance matrix of parallel lines is computed from the application of Carson’s equations and the Kron reduction method.
Series impedance of Overhead Lines
Line 1
Line 2
Figure 7.0

## Slide 54
    Parallel Overhead Lines
    With reference to Figure 7.0, the voltage drops in the two lines are given by:
    (62)
    The procedure for computing the phase impendence matrix for parallel underground distribution lines is the same as the parallel overhead lines
Series impedance of Overhead Lines

## Slide 55: Part 1: Overhead Lines
Series impedance of Overhead Lines
  Transposed Three-phase Lines
  Untransposed Distribution Lines
  Carson’s Equations
  Modified Carson’s Equations
  Primitive Impedance Matrix for Overhead Lines
  Phase Impedance Matrix for Overhead Lines
  Sequence Impedances
  Parallel Overhead Distribution Lines
Shunt Admittance of Overhead Parallel Lines
General Voltage Drop Equation

## Slide 56
Shunt Admittance of Overhead Parallel Lines
    General Voltage Drop Equation
    The shunt admittance of a line consists of the conductance and the capacitive susceptance.
    The conductance is usually ignored because it is very small compared to the capacitive susceptance.
    The capacitance of a line is the result of the potential difference between conductors

## Slide 57
Shunt Admittance of Overhead Parallel Lines
    Electric field of a charged round conductor
Figure 8.0

## Slide 58
Shunt Admittance of Overhead Parallel Lines
    Electric field of a charged round conductor
    A charged conductor creates an electric field that emanates outward from the center of the conductor.
    Lines of equipotential are created outward from the center of the conductor.
    A difference of potential between two points is a result of the electric field of the charged conductor.
    When the potential difference between two points is known, then the capacitance between the two points can be computed.

## Slide 59
Shunt Admittance of Overhead Parallel Lines
    General Voltage Drop Equation
(63)
Figure 9.0

## Slide 60: Part 1: Overhead Lines
Series impedance of Overhead Lines
  Transposed Three-phase Lines
  Untransposed Distribution Lines
  Carson’s Equations
  Modified Carson’s Equations
  Primitive Impedance Matrix for Overhead Lines
  Phase Impedance Matrix for Overhead Lines
  Sequence Impedances
  Parallel Overhead Distribution Lines
Shunt Admittance of Overhead Parallel Lines
General Voltage Drop Equation

## Slide 61
Shunt Admittance of Overhead Parallel Lines
    Definition of Terms
permittivity of the medium
permittivity of free space F/meter
relative permittivity of the medium
charge density on conductor cb/meter
distance between conductor and conductor (ft.)
distance between conductor and conductor (ft.)
radius () of conductor

## Slide 62
Shunt Admittance of Overhead Parallel Lines
    Conductors and Images
Figure 10.0

## Slide 63
Shunt Admittance of Overhead Parallel Lines
    The method of conductors and their images is employed in the calculation of the shunt capacitance of overhead lines. This is the same concept that was used for calculating series impedances in the general application of Carson’s Equations.
(64)
when assuming:
(66)
(65)

## Slide 64
Shunt Admittance of Overhead Parallel Lines
    where
The first step is to create the primitive potential coefficient matrix, where the elements of the primitive potential coefficient matrix are given by
distance of the conductor to its image (ft)
distance of the conductor to the image of conductor (ft)
distance of the conductor to conductor (ft)
radius of conductor (ft)
mile/F (67)
mile/F (68)

## Slide 65
Shunt Admittance of Overhead Parallel Lines
    After reducing the primitive potential matrix through Kron reduction, we obtain the potential matrix .
    The shunt capacitance matrix is the inverse of the potential matrix.
(69)
  The Shunt admittance matrix is given by
    (70)
    where

## Slide 66: Part 2: Underground Lines
Underground lines
    Series impedance of Underground Lines
  Concentric Neutral Cable
    Tape Shielded Cables
  Shunt Admittance of Underground Lines
  Concentric Neutral Cable
    Tape Shielded Cables
  Sequence Admittance
  Parallel Underground Distribution Lines
    Series impedance
    Shunt Admittance

## Slide 67: Part 2: Underground Lines
Underground lines
    Series impedance of Underground Lines
  Concentric Neutral Cable
    Tape Shielded Cables
  Shunt Admittance of Underground Lines
  Concentric Neutral Cable
    Tape Shielded Cables
  Sequence Admittance
  Parallel Underground Distribution Lines
    Series impedance
    Shunt Admittance

## Slide 68
  Series impedance of Underground Lines
        Concentric Neutral Cable
      Figure shows the detail of a concentric neutral cable
Figure 11.0

## Slide 69
  Series impedance of Underground Lines
      Concentric Neutral Cable
      In order to apply the Carson’s equations, the following data needs to be extracted from a table of underground cables. (Appendices A and B in the book)
diameter of phase conductor (inches)
nominal diameter over the concentric neutrals of the cable (inches)
diameter of a concentric neutral strand (inches)
geometric mean radius of the phase conductor (feet)
geometric mean radius of a neutral strand (feet)
resistance of the phase conductor (Ω/mile)
resistance of a solid neutral strand (Ω/mile)
number of concentric neutral strands

## Slide 70
  Series impedance of Underground Lines
      Concentric Neutral Cable
      The GMR of the phase conductor and a neutral strand are obtained from the standard table of the conductor data (Appendix A).
      The equivalent GMR of the concentric neutral is computed using the equation
        ft (71)
      where is the radius of a circle passing through the center of the concentric neutral strands given by:
        ft (72)

## Slide 71
      The equivalent resistance of the concentric neutral is:
      Ω/mile (73)
  Series impedance of Underground Lines
      Concentric Neutral Distances
CN to its own phase conductor:
CN to adjacent CN:
Center-to-Center of phase conductors
CN to adjacent phase conductor:
(74)

## Slide 72: Part 2: Underground Lines
Underground lines
    Series impedance of Underground Lines
  Concentric Neutral Cable
    Tape Shielded Cables
  Shunt Admittance of Underground Lines
  Concentric Neutral Cable
    Tape Shielded Cables
  Sequence Admittance
  Parallel Underground Distribution Lines
    Series impedance
    Shunt Admittance

## Slide 73
  Series impedance of Underground Lines (Contd…)
        Tape Shielded Cables
      The tape shielded cable consists of a central conductor covered by a thin layer of non-metallic semi conducting screen to which is bonded the insulating material.
      The insulation is covered by a semiconducting insulation screen. The shield is bare copper tape.
      An insulating jacket encircles the tape shield.

## Slide 74
  Series impedance of Underground Lines (Contd…)
        Tape Shielded Cables
Figure 12.0

## Slide 75
  Series impedance of Underground Lines (Contd…)
      Tape Shielded Cables
      Parameters of the tape shielded cable are:
Modified Carson’s Equations will be applied to calculate:
  self impedances of the phase conductor and the tape shield
  mutual impedance between the phase conductor and the tape shield.
The resistance and GMR of the phase conductor are found in a standard table of conductor data. (Appendix A in this book)
diameter of phase conductor (inches)
outside diameter of the tape shield (inches)
outside diameter over jacket (inches)
thickness of copper tape shield (millimeters)

## Slide 76
  Series impedance of Underground Lines (Contd…)
      Tape Shielded Cables
  The resistance of the tape shield is given by:
      Ω/mile (75)
      Assumptions:
        Temperature is 50 degrees C
        Resistivity is 100 Ω-meter
    The GMR of the tape shield is the radius of a circle passing through the middle of the shield and is given by:
    ft (76)

## Slide 77
  Series impedance of Underground Lines (Contd…)
      Tape Shielded Cables
      The various spacings between a tape shield and the conductors and other tape shields are as follows:
        Tape shield to its own phase:
        radius to midpoint of the shield (feet)
        Tape shield to an adjacent tape shield:
        center-to-center distance of the phase conductors (feet)
        Tape shield to an adjacent phase or neutral conductor:
feet
where center-to-center distance between phase conductors

## Slide 78: Part 2: Underground Lines
Underground lines
    Series impedance of Underground Lines
  Concentric Neutral Cable
    Tape Shielded Cables
  Shunt Admittance of Underground Lines
  Concentric Neutral Cable
    Tape Shielded Cables
  Sequence Admittance
  Parallel Underground Distribution Lines
    Series impedance
    Shunt Admittance

## Slide 79
  Shunt Admittance of Underground Lines
      Concentric Neutral Cable
      Figure shows a basic concentric neutral cable with center conductor being the phase conductor and the concentric neutral strands equally displaced around a circle of radius of Rb
Figure 13.0

## Slide 80
      Concentric Neutral Cable
        where
        = Radius of a circle passing through the centers of the neutral strands
        = Diameter of the phase conductor
        = Diameter of a neutral strand
        = Total number of neutral strands
  Shunt Admittance of Underground Lines

## Slide 81
      Concentric Neutral Cable
    The concentric neutral strands are grounded so that they are all at the same potential.
    Since they are all at the same potential, it is only necessary to determine the potential difference between the phase conductor and strand .
(77)
where
  Shunt Admittance of Underground Lines

## Slide 82
  Shunt Admittance of Underground Lines
      Concentric Neutral Cable
      The voltage drop from the phase conductor to neutral strand is then given by
        (78)
      The electric field of a cable is confined to the insulation material. Cross-Linked Polyethlyene is a very popular insulation material.
      If the minimum value of relative permittivity is assumed, the equation for shunt admittance of the concentric neutral cable is given by
        S/mile (79)

## Slide 83
  Typical Values of Relative Permittivity
        Table 1.0
Material | Relative Permittivity
Polyvinyl Chloride (PVC) | 3.4-8.0
Ethylene-Propylene Rubber (EPR) | 2.5-3.5
Polyethylene (PE) | 2.5-2.6
Cross-Linked Polyethylene (XLPE) | 2.3-6.0

## Slide 84: Part 2: Underground Lines
Underground lines
    Series impedance of Underground Lines
  Concentric Neutral Cable
    Tape Shielded Cables
  Shunt Admittance of Underground Lines
  Concentric Neutral Cable
    Tape Shielded Cables
  Sequence Admittance
  Parallel Underground Distribution Lines
    Series impedance
    Shunt Admittance

## Slide 85
  Shunt Admittance of Underground Lines
(Contd….)
      Tape Shielded Cables
      The tape-shielded cable is shown in Figure 14.0. is the radius of the circle passing through the center of the tape-shield.
Figure 14.0

## Slide 86
  Shunt Admittance of Underground Lines
(Contd….)
      Tape Shielded Cables
      As with the concentric neutral cable, the electric field is confined to the insulation so that the relative permittivity of Table 1.0 will apply.
      The tape-shielded conductor can be visualized as a concentric neutral cable where the number of strands has become infinite.
      Therefore, the equation for the shunt admittance of a tape-shielded conductor becomes:
      S/mile (80)

## Slide 87: Part 2: Underground Lines
Underground lines
    Series impedance of Underground Lines
  Concentric Neutral Cable
    Tape Shielded Cables
  Shunt Admittance of Underground Lines
  Concentric Neutral Cable
    Tape Shielded Cables
  Sequence Admittance
  Parallel Underground Distribution Lines
    Series impedance
    Shunt Admittance

## Slide 88
  Sequence Admittance
      Sequence Admittance of a three phase line
      The sequence admittances of a three-phase line can be determined in much the same manner as the sequence impedances.
      Assume that the 3 X 3 admittance matrix is given in S/mile. Then the three phase capacitance currents as a function of the line-to ground voltages is given by:
(81)
(82)

## Slide 89
  Sequence Admittance
      Sequence Admittance of a three phase line
(83)
(84)
Applying symmetric component transformations:
Sequence admittance matrix given by:

## Slide 90
        Sequence Admittance of a three phase line
    For a three-phase overhead line with unsymmetrical spacing, the sequence admittance matrix will be full (non-zero off diagonal terms).
    However, a three-phase underground line with three identical cables will only have the diagonal terms since there is no “mutual capacitance” between phases.
    In fact, the sequence admittances will be exactly the same as phase admittances.
  Sequence Admittance

## Slide 91: Part 2: Underground Lines
Underground lines
    Series impedance of Underground Lines
  Concentric Neutral Cable
    Tape Shielded Cables
  Shunt Admittance of Underground Lines
  Concentric Neutral Cable
    Tape Shielded Cables
  Sequence Admittance
  Parallel Underground Distribution Lines
    Series impedance
    Shunt Admittance

## Slide 92
    Series Impedance of Parallel Underground Distribution Lines
    The procedure for computing the phase impedence matrix for parallel underground distribution lines is the same as the parallel overhead lines.
    Carson’s equations are applied to find the primitive impedance matrix.
    The Kron reduction is applied to find the final impedance matrix.

## Slide 93: Part 2: Underground Lines
Underground lines
    Series impedance of Underground Lines
  Concentric Neutral Cable
    Tape Shielded Cables
  Shunt Admittance of Underground Lines
  Concentric Neutral Cable
    Tape Shielded Cables
  Sequence Admittance
  Parallel Underground Distribution Lines
    Series impedance
    Shunt Admittance

## Slide 94
Shunt Admittance of Underground Parallel Lines
    Computation of shunt admittance of underground lines is quite simple.
    The electric field created by the charged phase conductor does not link to the adjacent conductors because of the presence of concentric neutrals or the tape shield.
    As a result, the shunt admittance matrix for parallel underground lines will consist of diagonal terms only.

## Slide 95
Shunt Admittance of Underground Parallel Lines
    The diagonal terms for concentric neutral cables are given by:
S/mile (85)
where
radius of circle through center of neutral strands (feet)
radius of the center phase conductor (feet)
radius of neutral strands (feet)
number of neutral strands

## Slide 96
Shunt Admittance of Underground Parallel Lines
    The diagonal terms for tape-shielded cables are given by:
S/mile (86)
where
radius of circle through center of neutral strands (feet)
radius of center of phase conductor (feet)